## Slide 1
ATTENTION: See Adjustment for AIA/ICC
When presenting for ICC credits, hide slide 3 (AIA).
When presenting for AIA credits, hide slide 4 (ICC).

## Slide 2
Buildings and Homes in Flood Hazard Areas:
Connections at or Below Design Flood Elevations

## Slide 3: Buildings and Homes in Flood Hazard Areas Connections at or Below Design Flood Elevations
Simpson Strong-Tie Company Inc.
PO Box 10789 Pleasanton, CA 94588
The American Institute of Architects
This program qualifies for 1.0 LU/HSW Hour
Simpson Strong-Tie is a registered provider of AIA-approved continuing education under Provider Number “Insert Provider Number”. All registered AIA CES Providers must comply with the AIA Standards for Continuing Education Programs. Any questions or concerns about this provider or this learning program may be sent to AIA CES (cessupport@aia.org or (800) AIA 3837, Option 3).
This learning program is registered with AIA CES for continuing professional education. As such, it does not include content that may be
deemed or construed to be an approval or endorsement by the AIA of any material of construction or any method or manner of handling,
using, distributing, or dealing in any material or product.
AIA continuing education credit has been reviewed and approved by AIA CES. Learners must complete the entire learning program to
receive continuing education credit. AIA continuing education Learning Units earned upon completion of this course will be reported to
AIA CES for AIA members. Certificates of Completion for both AIA members and non-AIA members are available upon completion of the course.
©2020 Simpson Strong-Tie

## Slide 4: Credit Information, cont.
IACET Accreditation Information
Simpson Strong-Tie® has been accredited as an Authorized Provider by the International Association for Continuing Education and Training (IACET), 7918 Jones Branch Drive, Suite 300, McLean, VA 22102; (703) 506-3275. In obtaining this approval, Simpson Strong-Tie® has demonstrated that it complies with the ANSI/IACET Standard which is recognized internationally as a standard of good practice. As a result of their Authorized Provider accreditation status, Simpson Strong-Tie® is authorized to offer IACET CEUs for its programs that qualify under the ANSI/IACET Standard.
This course offers 0.1 CEU (1 hour of credit).
Notes: Review the submission process for audiences requiring IACET CEU credits.
For those seeking IACET credit, they must take and pass the online test. They must self-report CEU credits to their certifying organization or agency.
Explain the credits awarded: IACET: 0.1 (Equivalent to 1 hour) CEUs.

## Slide 8
Learning Objectives
After completing this course, you will be able to:
Specify and detail flood resistant construction in any context.
Choose the correct anchors, fasteners, and connectors.
Design safe structures that resist flotation, collapse, or permanent lateral movement during flood events.
Communicate effectively about flood issues and flood resistant design.
Purpose:
This course explores flood requirements, concepts and details of flood resistant construction, the use of anchors, fasteners, and connectors in flood resistant buildings, and the relevant terminology, codes and standards that should be used.
Notes: Say: Flooding is an increasingly frequent and costly danger and flood prone areas are expanding in many areas of the US as storms worsen, floodplains expand, and sea levels rise. As a result, many homes and buildings which were poorly built, built without flood resistant construction, or inappropriately detailed have been swept away, completely demolished, or significantly damaged. This course begins with an overview of flood requirements and then explores the concepts and details of flood resistant construction, provides detailed advice on how anchors, fasteners, and connectors can be used to create flood resistant buildings, and records the relevant terminology, codes and standards that should be used when consulting experts and authorities and designing flood resistant buildings.
Learning Objectives:
At the end of this program, participants will be able to:
specify and detail the appropriate approach to flood resistant construction in any context
choose and locate the correct anchors, fasteners, and connectors when designing flood resistant structures
design safe structures that are connected and anchored to resist flotation, collapse, or permanent lateral movement during flood events, and
communicate effectively and accurately with flood construction experts and authorities by using the correct terminology.
This section will outline some of the basic terminology that designers should become familiar with in order to communicate effectively with authorities and flood design specialists.

## Slide 9
Introduction and Terminology
Notes: Say: Let's start by looking at the most common fastener used with Simpson Strong-Tie connectors: the nail.

## Slide 10
Introduction and Terminology
Floods are the most common and most deadly natural disaster in the US.
In the past 5 years, all states have had at least one significant flood and 21 states have had frequent flooding.
Floodplains are dynamic and flood maps must constantly be updated.
Introduction
Notes: Say: Floods are the most common and most deadly natural disaster in the US and the world, and the situation is worsening.
In the past 5 years, all states have had at least one significant flood and 21 states have had frequent flooding.
People have settled near water for the whole of history. Nearly 50% of the U.S. population is within fifty miles of a coastline and there are more than 3.5 million miles of streams and rivers in the U.S. Floodplains are dynamic and flood maps such as those created by the Federal Emergency Management Agency (FEMA) must constantly be updated.
Homeowners insurance does not typically cover flood damage or loss.

## Slide 11
Introduction and Terminology
Hurricane Harvey damaged or destroyed over 200,000 homes.
Superstorm Sandy damaged more than 305,000 homes, caused more than $60B in damage.
Floods cause an average of $6B in property damage, claim 140 lives annually.
The Cost of Flooding
Notes: Say:
Hurricane Harvey damaged or destroyed over 200,000 homes and businesses with floods that resulted from 30-50 inches (760 mm. to 1250 mm.) of rainfall.
Superstorm Sandy, a large flood event, damaged more than 305,000 homes resulting in more than $60B in damage.
The U.S. Geological Survey notes that floods cause an average of $6B in property damage, claim 140 lives, and prompt more Presidential disaster declarations per year than any other hazard.

## Slide 12
Terminology
“Minor” Floor Mitigation Measures
acquisition of flood-prone properties
flood proofing of basements
elevating heating and air conditioning units
elevating buildings (image)
constructing new buildings above current or predicted flood elevations
forbidding new or re-construction in flood prone areas
Notes: Say: Flood mitigation considerations can be minor or major and they include:
the acquisition of flood-prone properties through voluntary buyouts or sellouts and/or the relocation of buildings or even communities to mitigate the problem completely
  In the past 30 years, however, FEMA has funded fewer than 45,000 voluntary buyouts of flood-prone properties.
flood proofing of basements
elevating heating and air conditioning units
elevating entire buildings or structures (image)
constructing new buildings well above current or predicted design elevation requirements in anticipation of future events, and
forbidding new or re-construction in floodplain or flood prone areas.

## Slide 13
Terminology
“Major” Mitigation Measures
Norfolk Virginia has rewritten its entire zoning ordinance to deal with flooding.
The city of Miami is considering abandoning an entire neighborhood to the sea because of flooding.
Houston, San Francisco, and New Orleans are creating new huge floodwater catchment areas, reconstructing wetlands, and creating major coastal defenses.
Notes: Say: The city of Norfolk Virginia has rewritten its entire zoning ordinance because of issues with frequent severe flooding.
The new ordinance contains a universal requirement that any new or expanding development must situate its ground floor 1.5 to 3′ (450 to 900mm.) above flood level as well as dictating where new development may be located.
The city of Miami is considering abandoning an entire neighborhood because of the increasing frequency of flooding which is due primarily to sea level rise in their case. Real estate values on the coast have dropped significantly and interior land prices have risen as people move inland to avoid danger.
Cities such as Houston, San Francisco, and New Orleans are creating new huge floodwater catchment areas, reconstructing wetlands, and creating major coastal defenses.

## Slide 14
Terminology
Designers must understand flood related terminology.
The next few slides will explain some of the most basic terms.
Notes: Say: To communicate effectively with flood design experts and to understand flood construction ordinances and maps, etc., accurately it is critical that designers understand flood related terminology that describes the nature and severity of flood events, flood zones, and flood resistant construction.
The next few slides will cover some of the most basic terminology that building designers should become fluent with.

## Slide 15
Terminology
Notes: Do: Point out the various zones and terms such as BFE.

## Slide 16
Terminology
Special Flood Hazard Areas (SFHAs)
SFHAs are high-risk flood areas which include:
V / VE
Coastal A / AE
A / AE or X.
A number after the letter refers to the base flood elevation (BFE); the elevation of surface water resulting from a flood that has a 1% chance of equaling or exceeding that level in any given year.
Notes: Say: Coastal A zones have higher wave heights of 1½’-3’. (470mm. to 1M.)
A zones are high risk zones defined as an SFHA where the land is subject to flooding from riverine or coastal sources subject to wave heights of less than 1½’.
X zones are low and moderate risk zones. Flood insurance is not mandatory in these zones but it is highly advisable as 25% of all flood insurance claims occur outside of A or V zones.

## Slide 17
Terminology
V Zones
V zones are coastal high hazard areas extending from offshore to an inland limit of a primary frontal dune.
In many cases, the landward limit has an unclear definition of the primary frontal dune.
V zones are well known along the Atlantic, Gulf, and Pacific coasts.
Image Placeholder
U.S. Air Force photo by Michael Peterson via vandenberg.af.mil/News
Notes: Say: V zones are high velocity zones defined as an SFHA in a coastal high hazard area extending from offshore to an inland limit of a primary frontal dune along an open coast or any other area subject to high velocity wave action greater than 3’ (1M.)
In many cases, the landward limit is defined by an unclear definition of the primary frontal dune, rather than by analysis of water level or wave conditions.
V zones are well known along the Atlantic, Gulf, and Pacific coasts of the U.S. However, waves on southern Lake Michigan reached ˃20′ (6M.), the second highest official reading for that lake on record during Superstorm Sandy.

## Slide 18
Terminology
A and X Zones
Coastal A zones have wave heights of 1½’-3′.
A zones are high risk zones where the land is subject to flooding from riverine or coastal sources subject to wave heights of less than 1½’.
X zones are low and moderate risk zones.
Notes: Say: Coastal A zones have higher wave heights of 1½’-3’. (470mm. to 1M.)
A zones are high risk zones defined as an SFHA where the land is subject to flooding from riverine or coastal sources subject to wave heights of less than 1½’.
X zones are low and moderate risk zones. Flood insurance is not mandatory in these zones but it is highly advisable as 25% of all flood insurance claims occur outside of A or V zones.

## Slide 19
Terminology
Floodways
A floodway is the stream and floodplain portion that conveys floods without raising the water surface elevation higher than a designated elevation.
Notes: Say: A floodway is the stream and floodplain portion that conveys floods without raising the water surface elevation higher than a designated elevation.

## Slide 20
Terminology
Floodways (cont’d)
Floodways vary in scale and definition.
Determine whether the buildings are in a current or future one that may grow.
FEMA flood maps can be a good source of information regard current and future flood status.
Notes: Say: Floodways vary in scale and definition. Some are well defined and relatively local (upper image) while others are very large, not as well defined, and cover vast areas (lower image).
Designers should determine whether they are designing buildings in a current floodway, a future one, or in one that may grow from looking like the upper one to the lower one over time.
As noted previously, because of continuously shifting weather patterns and behaviours and the shifting of flood conditions, sizes, and locations FEMA is constantly redrawing its flood maps and these can be a good source of information as to the flood status in a specific location at a particular time.
The current pattern of flood zones and floodways and a considerable amount of other flood related information can be accessed here.

## Slide 21
Terminology
Freeboard
Freeboard is an additional amount of height above the BFE used as a factor of safety.
In normal flood protection design a freeboard of 1′ to 2′ is common.
The higher the freeboard, the less flood insurance costs.
Notes: Say: Freeboard is an additional amount of height above the BFE used as a factor of safety in determining the level at which a structure’s lowest floor must be elevated or flood proofed to be in accordance with state or community floodplain management regulations.
In essence, it is the additional height that the structure is protected from flood waters above the BFE. In normal flood protection design a freeboard of 1 to 2′ (300 to 600mm.) is common although there may be instances when this should be increased if future flood levels are not certain.
There could be instances where the original design freeboard has been eliminated by increases in flood levels and this could mean the structure must be raised even further.
The higher the freeboard used for the design, the less the flood insurance will cost the owner of the structure.

## Slide 22
Terminology
Freeboard (cont’d)
Freeboard is the dimension between the white coconut layer that represents the flood wave tops and the red element which represents the underside of the house itself.

## Slide 23
General Flood Requirements
Notes: Say: Let's start by looking at the most common fastener used with Simpson Strong-Tie connectors: the nail.

## Slide 24
General Flood Requirements
The National Flood Insurance Program (NFIP) for new construction and major improvements a flood-prone area requires that buildings should be:
Adequately anchored to prevent flotation, collapse, or lateral movement
constructed with flood resistant materials, and
constructed to minimize flood damages.
NFIP also requires that the community be constructed according to the criteria of floodplain construction.
Notes: Say: The National Flood Insurance Program (NFIP) Section 60.3(a)(3) states that if a proposed building site is in a flood-prone area, all new construction and substantial improvements shall be:
designed (or modified) and adequately anchored to prevent flotation, collapse, or lateral movement of the structure resulting from hydrodynamic and hydrostatic loads, including the effects of buoyancy
constructed with materials resistant to flood damage, and
constructed by methods and practices that minimize flood damages.
Flooding is the only natural disaster for which the federal government provides insurance through FEMA’s NFIP. According to the NFIP, to be eligible for flood insurance, there is a requirement that the community be constructed according to the criteria of floodplain construction.

## Slide 25
General Flood Requirements
Flood-Resistant Construction Requirements
International Residential Code® (IRC)
R322.1 Flood-Resistant Construction. Applies to all buildings and structures constructed in A or V zones and coastal A zones
R301.2.4/R322.1…Exception: buildings and structures in floodways shall be designed and constructed in accordance with American Society of Civil Engineers (ASCE) 24.
International Building Code® (IBC) 2000–2018
1612.4/1612.2 all buildings in flood hazard areas, including coastal high-hazard areas and coastal A zones, shall be in accordance with Chapter 5 of ASCE 7 and ASCE 24.
Notes: Say: The National Flood Insurance Program (NFIP) Section 60.3(a)(3) states that if a proposed building site is in a flood-prone area, all new construction and substantial improvements shall be:
designed (or modified) and adequately anchored to prevent flotation, collapse, or lateral movement of the structure resulting from hydrodynamic and hydrostatic loads, including the effects of buoyancy
constructed with materials resistant to flood damage, and
constructed by methods and practices that minimize flood damages.
Flooding is the only natural disaster for which the federal government provides insurance through FEMA’s NFIP. According to the NFIP, to be eligible for flood insurance, there is a requirement that the community be constructed according to the criteria of floodplain construction.

## Slide 26
General Flood Requirements
Flood-Resistant Construction Requirements (cont’d)
The NFIP, IRC, and ASCE 24 all require structural systems to be designed to resist flotation, collapse, or permanent lateral movement from flooding.
IRC 2000–2018
  R322.1.2 Structural systems…shall be designed, connected, and anchored to resist flotation etc. due to structural loads and stresses from flooding …..
ASCE 24-05/14 (referenced by the IBC and for all buildings in floodways)
  1.5.1 General. New construction or substantial improvements shall be designed, constructed, connected, and anchored to resist flotation, collapse, or permanent lateral movement…
  1.6.1 Design and construction of structures located in flood hazard areas shall consider all flood-related loads and conditions…
Notes: Say: The NFIP, IRC, and ASCE 24 all require structural systems to be designed, connected, and anchored to resist flotation, collapse, or permanent lateral movement from flooding. The following are excerpts from these codes, but designers should familiarize themselves with the full text.
IRC 2000–2018
R322.1.2 Structural systems…of all buildings and structures shall be designed, connected, and anchored to resist flotation, collapse, or permanent lateral movement due to structural loads and stresses from flooding equal to the DFE (design flood elevation).
ASCE 24-05/14 (referenced by the IBC and for all buildings in floodways)
1.5.1 General. New construction or substantial improvements (50% or greater) shall be designed, constructed, connected, and anchored to resist flotation, collapse, or permanent lateral movement…
1.6.1 Design and construction of structures located in flood hazard areas shall consider all flood-related loads and conditions…

## Slide 27
General Flood Requirements
Flood-Resistant Construction Requirements (cont’d)
Note how many lateral and vertical forces there can be from the water alone.
Notes: Say: Flood-resistant construction must resist the flood forces noted in the diagrams
Note how many forces there can be from the water alone and how some of them are horizontal while others are vertical (uplift).

## Slide 28
General Flood Requirements
Flood-Resistant Construction Requirements (cont’d)
During storms, buildings are also subject to wind-related forces.
Connections must be able to deal with wind and water forces.
Notes: Say: Designers should also keep in mind that, especially during storms, buildings are subject to significant wind-related forces as well; all attachments and connections must be able to deal with both sets of forces simultaneously.

## Slide 29
General Flood Requirements
Flood-Resistant Construction Requirements (cont’d)
Continuous Load Path
All loads and forces must be continuously transferred through the structure to the base of the foundation.
Links must transfer the loads without breaking or failing.
Notes: Say: Providing a Continuous Load Path
All loads and forces must be continuously transferred through the structure to the base of the foundation, and thus all the links in the path must be strong enough to transfer the loads without breaking or failing in any way. Below is a list of some of the critical links.
Link #1 – Roof Sheathing to Roof Framing
Link #2 – Roof Framing to Exterior Walls
Link #3 – Top Plate to Wall Studs
Link #4 – Wall Sheathing to Window Header
Link #5 – Window Header to Exterior Wall
Link #6 – Wall to Floor Framing
Link #7 – Floor Framing to Support Beam
Link #8 – Floor Support Beam to Foundation (Pile)

## Slide 30
General Flood Requirements
Flood-Resistant Construction Requirements (cont’d)
This home floated off its foundation, knocked into and damaged the adjacent house, and then floated 600 yards down the street.
Notes: Say: As an example of potential consequences for non-flood-resistant construction or insufficient connection to the foundations, this home floated off its foundation, knocked into and damaged the adjacent house, and then floated 600 yards (548 m) down the street.

## Slide 31
General Flood Requirements
Flood-Resistant Construction Requirements (cont’d)
This home totally collapsed from flooding forces.

## Slide 32
Review Question
There are several flood hazard areas, designated as V/VE, coastal A/AE, A/AE, and X.
What is a V zone and what can you recall about its distinct characteristics?

## Slide 33
Answer
V zones are high-velocity zones defined as a special flood hazard area (SFHA) in a coastal high-hazard area extending from offshore to an inland limit of a primary frontal dune along an open coast or any other area subject to high-velocity wave action greater than 3′ (1 m).
In many cases, the landward limit is defined by an unclear definition of the primary frontal dune rather than by analysis of water level or wave conditions.

## Slide 34
Flood Elevation Considerations

## Slide 35
Flood Elevation Considerations
Flood Design Level Considerations
The DFE is the elevation of flooding, including wave height, that is generally used for design.
The DFE = base flood elevation (BFE) + freeboard. Thus: The DFE will always be the BFE or higher.

## Slide 36
Flood Elevation Considerations
Flood Design Level Considerations
Insurance premiums drop when a higher floor level above BFE or DFE is selected.
Notes: Say: Note that insurance premiums drop when a higher floor level above BFE or DFE is selected.
As noted previously, a higher DFE means that a higher freeboard dimension has been used for the design of a structure.

## Slide 37
Flood Elevation Considerations
Flood Design Level Considerations
A 500 year flood is minimum for Class 4 in ASCE 24-14.
Consider:
climate change, sea level rise*,
there have been at least 25 500-year floods since 2010!
*$1 trillion of property and structures are at risk from a sea level rise of 2′ (expected by 2050).
Notes: Say:
Determining the Flood Event to Design for
Should you design to the 500-year flood?
This is now a minimum for Flood Design
Class 4 in ASCE 24-14.
Consider:
climate change, sea level rise*, etc., and
there have been at least 25 500-year floods since 2010!
*According to the National Climate Assessment study, more than $1 trillion of property and structures in the US are at risk of inundation from a sea level rise of 2′ (600 mm) above current sea level, which could be reached by 2050.

## Slide 38
Raise Foundations and Connections

## Slide 39
Raised Foundations and Connections
Raised Foundations / Elevated Building Requirements
ASCE 24-05/14
In coastal A and V zones, all connection points below the DFE, should address flood-related loads.
  4.4 The bottom of the lowest horizontal member is the elevation reference for the BFE plus freeboard, DFE, or 500-year flood, whichever is higher.
IRC R322.3.2
Elevation requirement for V zones and coastal A zones is:
  1.2. BFE plus 1′. The reference is the bottom of the lowest portion of all horizontal structural members supporting the lowest floor.
Designers should design to the strictest applicable standard.

## Slide 40
Raised Foundations and Connections
Timber Pile-to-Beam Connection Requirements
ASCE 24-05/14 4.0 Coastal High Hazard Areas and Coastal A Zones
  4.5.6.6/4.5.6.5 Timber Pile Connections: notching of pile tops shall not exceed 50% of the pile cross section.
Note the excessive pile notch.
Notes: Say:
ASCE 24-05/14 states:
4.0 Coastal High Hazard Areas and Coastal A Zones
  4.5.6.6/4.5.6.5 Timber Pile Connections: notching of pile tops shall not exceed 50% of the pile cross section.
Note that the pile in the image has been notched far in excess of the maximum allowable.

## Slide 41
Raised Foundations and Connections
Timber Pile-to-Beam Bearing Requirements
If the beam bearing beam is insufficient install an engineer designed bracket.
bracket
insufficient bearing
Notes: Say: If the bearing under the beam is insufficient (images), it is necessary to install an engineered bracket and to have the connection designed by an engineer.

## Slide 42
Raised Foundations and Connections
Timber Pile-to-Beam / Joist Connection
Bending steel in the field may cause fractures at the bend line.
Straps are NOT permitted to be attached to a piling.
ASCE 24-05/14 states:
4.5.6.6/4.5.6.5 Other pile-to-beam connections are acceptable…providing that they DO NOT depend upon nailing for attachment of individual members.
Notes: Say: Unless otherwise noted, bending steel in the field may cause fractures at the bend line. Fractured steel will not carry the load and must be replaced.
Straps are NOT permitted to be attached to a piling—there is no performance data available (i.e., this type of connection has not been tested).
In addition, ASCE 24-05/14 states:
4.5.6.6/4.5.6.5 Other pile-to-beam connections are acceptable…providing that they DO NOT depend upon nailing for attachment of individual members.
Straps do depend on nailing as indicated in the adjacent image.

## Slide 43
Raised Foundations and Connections
Timber Pile-to-Beam Connection
Wood perpendicular to the grain at bolt holes often tears.
ASCE 24-05/14 4.0 Coastal High Hazard Areas and Coastal A Zones
  Timber Pile Connections…bolts ⅝″ diameter, minimum…
Notes: Say: One common wood failure is the tearing of the wood perpendicular to the grain at bolt holes.
Note once again the significant notching of the piles in the left-hand image
ASCE 24-05/14 states:
4.0 Coastal High Hazard Areas and Coastal A Zones
  4.5.6.6/4.5.6.5 Timber Pile Connections…bolts ⅝″ diameter, minimum…

## Slide 44
Raised Foundations and Connections
Timber Pile-to-Beam Connection: 5/8” Bolts
Parallel to grain end distance requirements in uplift = 7 diameters
2x10
⅝″ bolt end and edge distance geometry factor 3.08 ÷ 4.34 = 0.71
Notes: Say: Parallel to grain end distance requirements in uplift = 7 diameters (see NDS 2015 table 12.5.1A).
NDS is the American Wood Council (AWC) National Design Specification® for Wood Construction.

## Slide 45
Raised Foundations and Connections
Timber Pile-to-Beam Connection: 5/8” Bolts (cont’d)

## Slide 46
Raised Foundations and Connections
Timber Pile-to-Beam Connection: Propriety Screw
Proprietary, hot-dip galvanized screw:
0.276″ diameter
suitable for heavy-duty marine and coastal applications.
installs from one side
no predrilling
no washers, nuts, or bolts
oversized 0.903″ diameter integral washer
Notes: Say: A proprietary, hot-dip galvanized screw is a 0.276″ diameter screw suitable for heavy-duty marine and coastal applications.
Installs from one side
No predrilling—no auger bits required
No need to purchase separate washers, nuts, and bolts
Oversized 0.903″ diameter integral washer eliminates the need for separate washers

## Slide 47
Raised Foundations and Connections
Timber Pile-to-Beam Connection: Propriety Screw (cont’d)
good for single and double stringers, square or round piles
ASTM A153 Class-C HDG coating suitable for coastal and marine environments (minimum ASCE 24 requirement), and
available in 4″, 6″, 8″, 10″, and 12″ lengths.
Notes: Say: These screws:
are good for single and double stringers (see connection options above)
are good for square or round piles
have an ASTM A153 Class-C HDG coating suitable for coastal and marine environments (the minimum ASCE 24 requirement), and
are available in lengths of 4″, 6″, 8″, 10″, and 12″.

## Slide 48
Raised Foundations and Connections
Timber Pile-to-Beam Connection: Proprietary Screw vs 5/8” Bolts
Uplift Comparison in a Continuous Beam
(¾″ bolts only bring load to 1,258# (larger diameter = more strength, but CΔ = geometry factor goes from 0.71 to 0.59)
Larger bolts must be a greater distance from the edge for full capacity.
Bolt holes closer to the edge reduce permitted load and need to be reduced by the geometry factor.
Wood connections are stronger when the load is spread out over a number of fasteners.
Designers should consider using more, smaller fasteners and fewer, larger ⅝″ bolts when possible.
Notes: Say:
Uplift Comparison in a Continuous Beam
(¾″ bolts only bring load to 1,258# (larger diameter offers more strength, but CΔ = geometry factor goes from 0.71 to 0.59)
Larger bolts must be a greater distance from the edge (7x the diameter) for full capacity because the bolt is more likely to fail (tear through the wood) without this additional edge distance. Because the size of the wood member doesn’t change, the bolt holes become closer to the edge and the load permitted would need to be reduced by the geometry factor.
Wood connections are stronger when the load is spread out over a number of fasteners. To accomplish this, designers should consider using more, smaller fasteners and fewer, larger ⅝″ bolts when possible. Further information is available here. (Accessed October 2020.)

## Slide 49
Raised Foundations and Connections
Timber Pile-to-Beam Connection
ASCE 24-05/14
4.0 Coastal High Hazard Areas and Coastal A Zones
Timber Pile Connections
  Other connections are acceptable if equal or superior to the applications.
  Connections shall be made with timber scabs or metal straps and headed bolts, or positive tension-resisting devices…
Notes: Say: ASCE 24-05/14 4.0 Coastal High Hazard Areas and Coastal A Zones
  Timber Pile Connections
  Other connections are acceptable provided they are equal to, or superior to, the applications.
  Connections shall be made with timber scabs or metal straps and headed bolts, or positive tension-resisting devices…

## Slide 50
Raised Foundations and Connections
Timber Pile-to-Beam Connection
Piling straps can be used:
where there is insufficient uplift resistance from the pile-to-beam connection, or
as another pile-to-beam option

## Slide 51
Raised Foundations and Connections
ASCE 24 Corrosion Resistance Requirements
ASCE 24-05/14 Flood Resistant Design and Construction
  5.1…Exposed materials, including connections, shall be capable of resisting corrosion..
  5.2.2.2 Noncorrosive Environments: straps and anchoring devices shall be stainless steel or hot-dip galvanized (HDG) after fabrication…
Therefore:
All exposed connectors and fasteners based on the IBC or in floodways shall meet the following guidelines:
Connectors: Batch/Post-HDG (ASTM A123, grade 95) or 316 stainless steel
Fasteners: HDG per ASTM A153, class C (2.1 mils/53 microns min.) or stainless steel
Notes: Say:
ASCE 24-05/14 Flood Resistant Design and Construction
5.0 Materials
  5.1…Exposed structural and nonstructural…materials, including connections, shall be capable of resisting…corrosion or decay due to precipitation, wind-driven water, salt spray, or other corrosive agents…
  5.2.2.2 Noncorrosive Environments…exposed...straps and anchoring devices shall be stainless steel or hot-dip galvanized (HDG) after fabrication…
Note:
ASTM A653, G185, and G90 connectors are hot-dip galvanized prior to fabrication.
Batch/Post-HDG connectors per ASTM A123, grade 95 are hot-dip galvanized after fabrication. (Amount of zinc varies with the thickness of the steel and must be ≥14 ga.)
Therefore:
All exposed connectors and fasteners based on the IBC or in floodways shall meet the following guidelines:
Connectors: Batch/Post-HDG (ASTM A123, grade 95) or 316 stainless steel
Fasteners: HDG per ASTM A153, class C (2.1 mils/53 microns min.) or stainless steel

## Slide 52
Raised Foundations and Connections
Building in a Flood Hazard Zone
This construction is relying solely on friction which is insufficient for flood resistance.
Notes: Say: Note the lack of hardware at all the connections. This construction is relying solely on friction to resist all horizontal and vertical forces. This would be insufficient during a flood, and this building would be likely swept off its piers.

## Slide 53
Raised Foundations and Connections
Concrete or Grout-Filled CMU Beam-to-Pile
Houses with concrete or masonry piers may use cast-in-place caps as illustrated.
Notes: Say: Many structures use concrete or masonry piers to support elevated framing. These piers function much like the wood piles that were reviewed previously.
They take both uplift and lateral forces from the framing above and transfer them to the foundation.
Options like the illustrated column caps are cast-in-place at the time of construction.

## Slide 54
Raised Foundations and Connections
Concrete to Grout-Filled CMU Beam-to-Pile Connection
Other options include a post-installed hold-down as above.
Piers must be constructed to resist the forces transferred into them with proper amounts of reinforcing and appropriate compressive strength.
Notes: Say: Other options may allow for a post installed or retrofit solution such as the hold-down shown here on the right.
It is important to note that the concrete and masonry piers must be constructed to resist the forces transferred into them.
They should have the proper amounts of reinforcing bar and appropriate compressive strength for the grout or concrete.

## Slide 55
Raised Foundations and Connections
Beam-to-Joist Connections Pre-Superstorm Sandy
FEMA detail prior to Superstorm Sandy showing H2.5-type connector.

## Slide 56
Raised Foundations and Connections
Beam-to-Joist Connections Pre-Superstorm Sandy (cont’d)
These connectors failed because they lacked the capacity to transfer the loads and forces.

## Slide 57
Raised Foundations and Connections
Beam-to-Joist Connections Pre-Superstorm Sandy (cont’d)
These connectors failed because they were too close to the edge.

## Slide 58
Raised Foundations and Connections
Beam-to-Joist Connections Pre-Superstorm Sandy (cont’d)
These connections failed because there was no corrosion protection on thin gauge straps.
316 stainless steel twist strap

## Slide 59
Raised Foundations and Connections
Beam-to-Joist Connections Pre-Superstorm Sandy (cont’d)
FEMA improved connections for elevated coastal residential buildings post Sandy
longer twist straps
straps applied to every joist
note other necessary hold-down connections
Notes: Say: FEMA detail after Superstorm Sandy showing a longer twist strap
Note: Straps must be applied to every joist as illustrated.
Note the other necessary hold-down connections as well.

## Slide 60
Raised Foundations and Connections
Beam-to-Joist Connections Pre-Superstorm Sandy (cont’d)
longer twist straps with proprietary structural screws, or
longer SS twist straps with SS ring shank nails
longer hot-dipped galvanized or SS twist straps with heavy-duty, proprietary, structural screws
OR

## Slide 61
Raised Foundations and Connections
Timber Pile Splice or Repair
Sometimes, after damage, structures must be brought to compliance with current codes since the BFE is likely higher. This means new piles or a proprietary jacket system to splice on a new pile section.
Notes: Say: Sometimes a home may require repairs after being damaged. When that occurs, structures must be brought to compliance with the current building code. If a structure was built many years back, it is highly possible that the BFE has become higher and the structure will need to be raised. That could mean removing current piles and installing new ones (often very costly and susceptible to material shortages) or using a proprietary jacket system to splice a new pile section on top of the existing one. This would bring the structure back to compliance with the current code and higher BFE.

## Slide 62
Raised Foundations and Connections
Concrete Pile Repair
Floodwaters can erode wood and concrete piles.
Repairs may involve shoring the structure and/or the erection of water barriers to establish dry working conditions.
Notes: Say: In other cases, floodwaters can erode piles, both wood and concrete.
Repairs can be costly and may involve shoring the structure to remove or replace sections of the pile.
This is time consuming and difficult and could even require the erection of water barriers to establish dry working conditions for new concrete.

## Slide 63
Raised Foundations and Connections
Concrete Pile Repair (cont’d)
Another option is a fiberglass jacket section which is used to encapsulate the damaged pile section.
The jacket is filled with either a cementitious or epoxy grout.
These repairs are long lasting and usually more durable than the original pile installation.
Notes: Say: Another repair option is to repair in place using a fiberglass jacket section.
As noted on the timber splice slide, the fiberglass jacket encapsulates the damaged section of the pile.
All the loose debris is removed first before encapsulation, then the jacket is filled with either a cementitious or epoxy grout, restoring its strength and load capacity.
These repairs are long lasting and usually more durable than the original pile installation.

## Slide 64
Review Question
The National Flood Insurance Program (NFIP) has three conditions for building sites in a flood-prone area.
Can you recall what they are?

## Slide 65
Answer
The NFIP requires that, to build in a flood prone area, buildings should be:
designed (or modified) and adequately anchored to prevent flotation, collapse, or lateral movement of the structure resulting from hydrodynamic and hydrostatic loads, including the effects of buoyancy
constructed with materials resistant to flood damage, and
constructed by methods and practices that minimize flood damages.

## Slide 66
Review Question
What are some of the upgraded design options for beam-to-joist connections that were created following Superstorm Sandy?

## Slide 67
Answer
Following Superstorm Sandy, because of the number of failures of the H2-5 (H2.5-type) connectors, these options came into use:
longer twist straps with proprietary structural screws
longer stainless-steel twist straps with stainless-steel ring shank nails
longer hot-dipped galvanized (HDG) or stainless-steel twist straps with heavy-duty, proprietary, structural screws

## Slide 68
Solid Foundations and Connections

## Slide 69
Solid Foundations and Connections
Solid Foundation Requirements
Solid foundations are:
usually used in A zones or coastal A zones
not permitted in V zones or in ASCE 24 design governed coastal A zones
NFIP recommends:
everything below BFE address flood-related loads even if the lowest floor is above the BFE
NB. Required concrete/masonry reinforcing not shown for clarity purposes
Notes: Say: Solid foundations are usually used in A zones or coastal A zones.
Solid foundations are not permitted in V zones or if the design is governed by ASCE 24 in coastal A zones.
The NFIP recommends that everything below the BFE, including the lowest floor, address flood-related loads even if the lowest floor is elevated above the BFE.
Note: Concrete/masonry reinforcing is not shown in this diagram for clarity purposes but is required per designer

## Slide 70
Solid Foundations and Connections
A Zone and Coastal A Zone Solid Foundation Requirements
IRC R322.2.1 Elevation requirement (A and coastal A zones):
Buildings and structures: elevate lowest floor to or above the BFE plus 1′ or the DFE.
Shallow flooding (A0 Zones): depth on flood insurance rate maps plus 1′ or not less than 3′
ASCE 24-05/14 Section 2.3: A zones: top of the lowest floor is the reference level
NFIP, IRC, and ASCE 24 all require structural systems to be designed, connected, and anchored to resist flotation, collapse, or permanent lateral movement from flooding.
IRC 2000–2018: R322.as above …..from flooding equal to the DFE.
ASCE 24-05/14: (referenced by the IBC and for all buildings in floodways)
1.5.1 New construction or substantial improvements: as above
1.6.1 …..structures located in flood hazard areas shall consider all flood-related loads and conditions…
Notes: Say:
IRC R322.2.1 Elevation requirement (A and coastal A zones):
Buildings and structures in flood hazard areas, including coastal A zones, shall have the lowest floor elevated to or above the BFE plus 1′ or the DFE.
Shallow flooding (A0 Zones): depth specified on flood insurance rate maps (FIRMs) plus 1′ (300 mm) or not less than 3′ (1 m) if the depth number is not specified.
ASCE 24-05/14 Section 2.3: In A zones, the top of the lowest floor is the reference level for minimum elevation.
NFIP, IRC, and ASCE 24 all require structural systems to be designed, connected, and anchored to resist flotation, collapse, or permanent lateral movement from flooding.
IRC 2000–2018: R322.1.2 Structural systems of all buildings and structures shall be designed, connected, and anchored to resist flotation, collapse, or permanent lateral movement due to structural loads and stresses from flooding equal to the DFE.
ASCE 24-05/14: (referenced by the IBC and for all buildings in floodways)
1.5.1 General. New construction or substantial improvements (50% or greater) shall be designed, constructed, connected, and anchored to resist flotation, collapse, or permanent lateral movement…
1.6.1 Design and construction of structures located in flood hazard areas shall consider all flood-related loads and conditions…

## Slide 71
Solid Foundations and Connections
Masonry Foundation Flood-Resistant Construction Requirements
ASCE 24-05/14
5.2.4 Masonry…shall comply with ACI 530/TMS 402…
ACI 530-08/13 referenced in ASCE 24 and 2000–2015 I-codes
TMS 402 (The Masonry Society), referenced in ASCE 24 and 2003–2018 I-codes
1.7.1/4.1.1 General.
  Masonry shall be designed to resist applicable loads.
  A continuous load path with adequate strength and stiffness, shall be provided….
Notes: Say:
ASCE 24-05/14
5.0 Materials
5.2.4 Masonry…shall comply with ACI 530/TMS 402…
ACI 530-08/13, referenced in ASCE 24 and 2000–2015 I-codes
TMS 402 (The Masonry Society), referenced in ASCE 24 and 2003–2018 I-codes
1.7.1/4.1.1 General. Masonry shall be designed to resist applicable loads. A continuous load path or paths, with adequate strength and stiffness, shall be provided to transfer forces from the point of application to the final point of resistance.

## Slide 72
Solid Foundations and Connections
Foundation to Sill Plate Connection
Sill plate must be adequately anchored to the foundation
Use anchor bolts, sill plate straps, structural adhesives with threaded rod, or a concrete/masonry screw approved for use with sill plates.
Required concrete/masonry reinforcement is not shown in this image for clarity
Notes: Say:
Connection below the top of the lowest horizontal member: the sill plate.
The sill plate has to be adequately anchored to the foundation (concrete or grout-filled concrete masonry unit, CMU).
This can be done with anchor bolts, sill plate straps, structural adhesives with threaded rod, or a concrete/masonry screw approved for use with sill plates.
Concrete/masonry reinforcement is not shown in this image for clarity but is required per designer.

## Slide 73
Solid Foundations and Connections
CMU Foundation to Wallace Failure Due to Flooding
This building was not anchored and was pushed off the foundation by a flood.

## Slide 74
Solid Foundations and Connections
Structural Anchoring Adhesives
Many structures need to be retrofitted.
Some installers simply prefer to post install anchorage to concrete or masonry.
There are epoxy and acrylic adhesives with different installation behaviors as well as several anchor types that can be used.
The next few slides describe adhesive and mechanical anchors that can attach framing members such as sill plates etc. to concrete or masonry piers.
Notes: Say: Many structures have a need to be retrofitted, and some installers simply prefer to post install anchorage to concrete or masonry. Both involve drilling holes into concrete or grout-filled concrete masonry.
There are different chemical formulations for these adhesives including epoxy and acrylic. They both exhibit similar performance when cured but different behaviors at installation. There are several anchor types that can be used with these materials.
The next few slides describe these adhesive anchors as well as mechanical anchors that can be used to attach framing members such as sill plates, beams, or connectors to concrete or masonry piers and the conditions that dictate which adhesive is appropriate in each case.

## Slide 75
Solid Foundations and Connections
Structural Anchoring Adhesives (cont’d)
Epoxies:
cure slower
are less expensive
have high strength in all applications
are limited to warmer weather
perform best at installation temperatures above 50°F
Acrylics:
set rapidly (1 hour at higher temperatures)
perform very well in colder installation conditions.
installation conditions determine which should be used.
drill hole, remove dust, inject adhesive and insert threaded rod.
use adhesives with code report and rated for use in cracked concrete
50°F (10°) C Minimum base material temperature
Notes: Say: Epoxies are a slower cure, usually a bit less expensive, and very high strength in all applications. They are limited to warmer weather and typically perform best at installation temperatures above 50°F (10°C).
Acrylic formulations are rapid set (1 hour at higher temperatures) and perform very well in colder installation conditions.
Both types can accomplish the anchor needs, but the installation conditions can affect which should be used. In either case, the components of the system include using a carbide bit to drill the hole and remove the dust, the adhesive to be injected into the hole, and the threaded rod inserted. It is best to use adhesives that have a code report and are rated for use in cracked concrete per the IBC.

## Slide 76
Solid Foundations and Connections
Structural Anchoring Adhesives for Various Applications
Adhesives anchor threaded rod, rebar, and dowels in various materials.
They deliver high-strength anchor grouting in a wide range of weather conditions as well as water-saturated concrete.
Notes: Say: Anchoring adhesives anchor threaded rod, rebar, and dowels in various materials.
They deliver high-strength anchor grouting in a wide range of weather conditions as well as water-saturated concrete.

## Slide 77
Solid Foundations and Connections
High-Strength Structural Adhesives for Post Installed Anchoring
Above table indicates adhesive anchors that replace standard ½″ and ⅝″ cast-in-place L bolts (1:1 replacement for both diameter and depth). Sill plates can also be anchored mechanically.
Notes: Say: This table shows the adhesive anchors that can replace standard ½″ (12.7 mm) and ⅝″ (15 mm) diameter cast-in-place L bolts used to anchor sill plates. It is a 1:1 replacement for both diameter and depth. Sill plates can also be anchored mechanically.

## Slide 78
Solid Foundations and Connections
Cast-in-Place Bolt Anchor Corrosion
These images show how corrosion can affect anchor bolts. The left-hand image is all that was left of a corroded bolt where the top showed above the surface but everything below had disappeared. The portion of the bolt showing in the right-hand photograph is too rusty and corroded to accept a nut or washer and cannot be used. It is important to use the right degree of corrosion resistance for the anchor in every case, especially in coastal zones.
Notes: Say: These images show how corrosion can affect anchor bolts. The left-hand image is all that was left of a corroded bolt where the top showed above the surface but everything below had disappeared. The portion of the bolt showing in the right-hand photograph is too rusty and corroded to accept a nut or washer and cannot be used. It is important to use the right degree of corrosion resistance for the anchor in every case, especially in coastal zones.

## Slide 79
Solid Foundations and Connections
Concrete and Masonry Screw Anchors
Use zinc-plated or mechanically galvanized concrete and masonry screw anchors for dry, interior applications.
Use stainless steel concrete and masonry screw anchors for exposed anchors or corrosive environments.
Anchors are a 1:1 replacement for equivalent diameter sill bolts in concrete or grout-filled CMUs with only 4½″ (115 mm) of embedment.
Notes: Say: Use zinc-plated or mechanically galvanized concrete and masonry screw anchors in dry, interior applications where corrosion is not a risk.
Use 304 and 316 stainless steel concrete and masonry screw anchors where the anchor is exposed or in applications that may be considered corrosive.
These anchors are a 1:1 replacement for equivalent diameter sill bolts in concrete or grout-filled CMUs with only 4½″ (115 mm) of embedment.

## Slide 80
Solid Foundations and Connections
Sill Plate-to-Rim Joist or Foundation-to-Framing Connection
Rim joist connection transfers lateral and uplift loads from framing to sill plate or foundation.
Many straps are designed to connect to concrete or masonry to wood.
Many reinforcing angles, with blocking, transfer loads from the rim joist to the sill plate.
The following slides show examples of load transfer to the next wood member or foundation.
Notes: Say: The rim joist connection must transfer lateral and uplift loads from the framing above to the sill plate or directly to the foundation.
There are many straps designed to connect to concrete or masonry on one end and wood on the other.
There are also many reinforcing angles along with the use of blocking to transfer loads from the rim joist to the sill plate.
You can find many standard details in various high wind publications. The following slides show some examples of how to transfer the load to the next wood member or foundation.

## Slide 81
Solid Foundations and Connections
Sill Plate-to-Framing Connection: Lateral Loads
This connection is not floor system dependent.
Connector spacing is independent of joist spacing.
Forces come from two directions simultaneously.
Notes: Say: Note: This connection is not floor system dependent and the connector spacing is independent of the joist spacing. Note that forces come from two directions at the same time.

## Slide 82
Solid Foundations and Connections
Sill Plate-to-Rim Joist Connection
Uplift connectors must bypass each other to prevent cross-grain tension of the band joist.
Notes: Say:

## Slide 83
Solid Foundations and Connections
Foundation Connections for Raised Homes
This house is being raised to meet new requirements from increasing flood heights.
Screw anchors cannot be installed.
Alternate connection solutions that can be utilized in place of the screws are shown on the following few slides.
Notes: Say: This image shows the raising of a house to meet new height requirements resulting from steadily increasing flood heights or storm activity.
Note that in this case, the screw anchors described earlier cannot be installed.
Alternate connection solutions that can be utilized in place of the screws are shown on the following few slides.

## Slide 84
Solid Foundations and Connections
Foundation Connections for Raised Homes (cont’d)
Floor system is separated from the old block foundation.
House is raised to permit the creation of a new foundation underneath it.
Notes: Say: First, the existing floor system is separated from the old block foundation,
Then the house is raised to permit the creation of a new foundation underneath it.

## Slide 85
Solid Foundations and Connections
Foundation Connections for Raised Homes (cont’d)
House is lowered, connectors resisting uplift loads (left images) and connectors resisting parallel forces (right) connect the house to the new foundation. Solution applies to both new construction and retrofits.
Notes: Say: Then the house is lowered back down, and connectors resisting uplift loads (left images) and connectors resisting parallel to plate forces (right images) are used to connect the house to the new foundation. This connector solution applies to new construction as well as retrofits.

## Slide 86
Solid Foundations and Connections
Flood Protection for Critical Infrastructure
Many facilities such as wastewater plants etc. that cannot be moved or raised require floodproofing and strengthening in order to meet new conditions and standards.
Notes: Say: There are certain buildings and facilities such as wastewater plants, electrical generation plants, bridges, and tunnels that cannot simply be moved or raised to provide flood protection.
These facilities often require floodproofing and strengthening in order to meet new conditions and standards and therefore to remain operational during a flood and long afterwards.

## Slide 87
Solid Foundations and Connections
Composite Strengthening for Flood Protection
FRPs :
offer great tension strength to reinforce structural members
can be shaped around existing members, and
use polymer resin to bond fabric to member
Notes: Say: These materials offer great tension strength in a lightweight material to reinforce structural members.
They can be shaped around the existing members such as beams, columns, and walls.
The materials are applied using a polymer resin that bonds the fabric to the structural member.

## Slide 88
Solid Foundations and Connections
Composite Strengthening for Flood Protection (cont’d)
FRPs reinforce at-risk facilities economically.
When used with installation of precured laminates carbon fiber is precured with resin into stiffer strips, epoxy paste is applied to the laminate, and then to surface of structural member.
Installation should be done by professionals.
Notes: Say: FRPs are an economical means of reinforcing at-risk facilities. Composite strengthening systems can also be used with the installation of precured laminates. In this case, the carbon fiber is precured with resin into stiffer strips. An epoxy paste is applied to the laminate, and then it is applied to the surface of the structural member. Note: The installation of these products can require extensive surface preparation and should be done by a certified installation contractor.

## Slide 89
Solid Foundations and Connections
Composite Strengthening for Flood Protection (cont’d)
Composite strengthening can be used:
as slab collector reinforcement
as opening trim reinforcement
as fabric for flexure/collector reinforcement, fabric for beam reinforcement
to stiffen walls and add flexural, shear, or tensile reinforcement
for new opening trim reinforcement
to wrap columns to achieve required strengthening, and
as coating for protection against exposure, corrosion, chemical attack, abrasion, etc.
Notes: Say:
Composite strengthening can be used for these purposes:
To add collector reinforcement for slabs
To add trim reinforcement to slab openings
As laminates or fabric for flexure and/or collector reinforcement, fabrics for shear stirrup reinforcement for beams
To stiffen walls and add flexural, shear, or tensile reinforcement
For trim reinforcement for new wall openings
To wrap columns to achieve required strengthening, possibly with additional near-surface-mounted laminate or fabric for flexure or for under-reinforced columns
As coatings for protection against exposure, corrosion, chemical attack, abrasion, etc.

## Slide 90
Summary

## Slide 91
Summary
The risk and impact of floods is steadily increasing in many areas, especially coastal areas.
The number of damaged or destroyed buildings and cost to repair/replace them has risen dramatically
There are many upgraded regulations and updated flood hazard zone boundaries.
Every construction project must verify which conditions and standards apply now and possibly in the future.
Many buildings must be substantially upgraded at great expense to meet current conditions.
There are now a number of improved connection products and methodologies.
Notes: Say:
As many aspects of our climate constantly change and storms become more frequent and ferocious and seas rise, the risk and impact of floods is steadily increasing in many areas of the country, especially coastal areas. This has, in turn, raised the overall number of structures that have been seriously damaged or destroyed and thus the cost to repair or replace them as well as the need to build or rebuild them in a much more flood resistant manner.
Much has been learned from these failures and a result there are now many upgraded regulations and updated flood hazard zone boundaries that designers should become fluent with. Because conditions constantly change and flood zone boundaries are flexible, every construction project must also verify which conditions and standards are relevant to their situation at the time of their construction and they should also forecast what further changes may be necessary in the future. There a number of situations where buildings were designed to meet the conditions at the time of their construction but which now must be substantially upgraded at great expense to meet current conditions and regulations and to qualify for insurance. It is wise to invest in the best possible construction in order to avoid these heavy costs in the future.
The lessons acquired the hard way from inadequate construction and connection methods have resulted in the development of a number of improved connection products and methodologies that designers can use to ensure they meet these new upgraded requirements and to deal with any future requirements or weather conditions.

## Slide 92
Summary
Many coastal homes are built on raised wooden pile foundations.
Connections between piles and houses must resist a number of lateral and vertical forces and create continuous path for all loads and storm forces from roof to foundation.
Designers can integrate purpose-designed proprietary screws, connectors, brackets, speciality straps, anchoring adhesives, timber and concrete pile repair or splicing products, specialty screws and anchors for masonry, concrete and timber pile foundations.
Manufacturers can assist designers in creating create safe and resistant structures, avoiding costly failures and reducing the cost of flood insurance for homeowners.
Notes: Say:
Many homes in coastal areas are built on raised foundations fabricated with a series of wooden piles. Connections between these piles and the rest of the house are critical and must resist a number of hydrostatic, wave, wind, and impact forces. These connectors must also be integrated into a full connection system that provides a continuous path for all loads and storm forces starting from the roof and extending down to the bearing point of the foundation.
Designers can integrate purpose designed proprietary screws, connectors, brackets, and speciality straps created for every unique connection situation as well as anchoring adhesives and timber and concrete pile repair or splicing products to create a fully linked connection system that can resist every conceivable flood situation. There are specialty screws and anchors which have been developed for masonry and concrete foundations as well as timber pile foundations.
The manufacturers and suppliers of these products can provide considerable advice and guidance on when and where each specific product should be utilized and this infers that if designers access this information and utilize these products appropriately they will be able to confidently create safe and resistant structures that will endure in every situation in the future and not only avoid the costly failures of the past but reduce the cost of flood insurance in the present.