## Slide 1
PLEASE READ
Dear Instructor,
This presentation is available in both AIA and ICC versions.
For AIA: Right click and un-hide slides 5 and 149
For ICC: Right click and un-hide slides 6 and 150
Slide 2 is an optional slide

## Slide 2: Welcome!
Welcome! We will begin in a few minutes.
Please be sure to sign the registration form to receive credit for attending today’s learning event.
Notes: Presenter’s Notes:

## Slide 3
Concrete Repair Installation
Proper Installation Practices for Successful Repairs
AIA Course Number:
AIA-RPSI0215
____________
AIA Provider: 50119826

## Slide 4: Credit Information
IACET Accreditation Information
Simpson Strong-Tie® has been accredited as an Authorized Provider by the International Association for Continuing Education and Training (IACET). As a result of their Authorized Provider accreditation status, Simpson Strong-Tie® is authorized to offer IACET CEUs for its programs that qualify under the ANSI/IACET Standard.
This course offers 0.2 CEU (2 hours of credit).
Notes: Review the submission process for audiences requiring IACET CEU credits.
For those seeking IACET credit, they must take and pass the online test. They must self-report CEU credits to their certifying organization or agency.
Explain the credits awarded: IACET: 0.2 (Equivalent to 2 hours) CEUs.

## Slide 5: Credit Information
AIA Member Information
This course is registered with AIA CES for continuing professional education. As such, it does not include content that may be deemed or construed to be an approval or endorsement by the AIA of any material of construction or any method or manner of handling, using, distributing, or dealing in any material or product. Upon completion of this course, Credit(s) earned will be reported to AIA CES for AIA members who pass the course and have entered their AIA member number on their Simpson profile page. A link to the Certificate of Completion will be available upon completion of this course. Only AIA LU/HSW will be reported.
This course offers 2 LU/HSW credits.
AIA Course Number: AIA- RPSI0215
Notes: Presenter Information
NOTE: Please be sure each attendee LEGIBLY signs the event sign-in sheet.
Say
All questions concerning proprietary products will be addressed after the conclusion of the AIA portion of the presentation. The meeting format is 110 minutes of content, followed by 10 minutes of Q & A.
Do
Explain the credits awarded for:
AIA: 2LU/HSW credit.
IACET: 0.2 (Equivalent to 2 hour) CEU credits.
Review the submission process for audiences requiring either AIA LU/HSW (health, safety and welfare) credits or CEU credits:
For those seeking AIA HSW credit, there is no test required. AIA members must be sure to provide their AIA member number on the sign-in sheet. Please make sure name, email and AIA member number are clearly printed so Simpson can report credits to the AIA on their behalf.
For those seeking IACET credit, they must take and pass the test. They must self-report CEU credits to their certifying organization or agency.

## Slide 6: Credit Information, cont.
ICC Member Information
This course has been approved by the International Code Council (ICC) for continuing professional education. For learners that complete this course, it is your responsibility to self-report your credits to the ICC. Please retain your Completion Certificate for your records.
Be sure that your ICC ID number is provided on the sign-in sheet or in your Simpson profile in order to have it displayed on your certificate.
This course offers 0.2 CEU (2 hours of credit).
ICC Course Number: 5740
Notes: Review the submission process for audiences requiring ICC CEU credits.
For those seeking ICC credit, there is no test required. ICC members must provide their ICC ID number on the sign-in sheet or in their Simpson profile in order to have it displayed on their certificate. It is the responsibility of the participant to self-report their credits to the ICC. Ask them to retain their Completion Certificate for their records.
Explain the credits awarded: ICC: 0.2 (Equivalent to 2 hours) CEUs.

## Slide 7: Additional Credit Offerings
Visit
strongtie.com/workshops
for more information
Course Name | CEUs | AIA | ICC
Introduction to Deck Design | 0.1 | ✔ | ✔
Introduction to Wind Design and the Wood Frame Construction Manual | 0.1 | ✔ | ✔
Shear Walls and Lateral Bracing in Light Frame Construction | 0.1 | ✔ | ✔
Understanding Restraint Rod Systems | 0.1 | ✔ | ✔
Cracking the Concrete Anchor Codes | 0.1 | ✔ | ✔
Concrete Deterioration | 0.1 | ✔ | ✔
Moment Frame Design | 0.1 | ✔ | ✔
Introduction to Wind Code Provisions and Meteorological Concepts | 0.1 | ✔ | ✔
Wind Design in Accordance with ASCE 7-10 | 0.1 | ✔ | ✔
Wood Framed Seismic Design 1: Code Provisions, Design Parameters | 0.1 | ✔ | ✔
Notes: Do
Explain that we have additional PK topics available that offer credit for ICC members and HSW credits for AIA members.
Explain that we have a library of online courses available in our Simpson Student Center that also offer ICC and AIA HSW credits. They can access our online courses at strongtie.com/workshops.

## Slide 8: Course Description
This course examines the advantages and disadvantages of certain repair materials and placement methods and provides installation recommendations and best practices at each phase in the repair process to increase the likelihood of a lasting, concrete repair.
Notes: Review course description.

## Slide 9: Learning Objectives
After completing this course, you will be able to:
Describe why a proper concrete assessment is critical to the success of a repair
Identify the benefits of proprietary repair materials
Explain how to properly prepare a surface so that it can accept a repair material
Choose which placement method would be ideal in certain repair situations
Notes: Do
Review the learning objectives for the course.
Inform students that the assessment questions will be based on these learning objectives. Slides that may contain information relevant to the test have a teal graduation cap located in the bottom-left corner.

## Slide 10: Concrete Repair References
International Concrete Repair Institute
American Concrete Institute
American Society for Testing and Materials
References:
Places to go for more information will be indicated throughout the course by this magnifying glass.
Notes: Throughout this course, we will reference some standards and guidelines that you can refer to for more information. These references will be indicated by this magnifying glass. Next, we will cover a few of the major organizations in the concrete industry.

## Slide 11: Concrete Repair References
International Concrete Repair Institute
American Concrete Institute
American Society for Testing and Materials
References:
www.icri.org
International Concrete Repair Institute (ICRI)
Notes: The International Concrete Repair Institute (ICRI) is the leading resource for education and information to improve the quality of repair, restoration, and protection of concrete and other structures. This organization mainly focuses on proper repairs as opposed to how to install and erect new concrete structures.

## Slide 12: Concrete Repair References
International Concrete Repair Institute
American Concrete Institute
American Society for Testing and Materials
References:
American Concrete Institute (ACI)
www.concrete.org
Notes: The American Concrete Institute (ACI) is a leading authority and resource for the development and distribution of standards and technical references for individuals and organizations involved in concrete design, construction, and materials.

## Slide 13: Concrete Repair References
International Concrete Repair Institute
American Concrete Institute
American Society for Testing and Materials
References:
American Society for Testing and Materials (ASTM)
www.astm.org
Notes: The American Society for Testing and Materials (ASTM) is an international standards organization that develops and publishes voluntary consensus technical standards for a wide range of materials, products, systems, and services.

## Slide 14: Concrete Basics

## Slide 15: Concrete Basics
In this lesson we will cover…
  What makes up concrete.
  How reinforced concrete combats compression and tension forces.
  Why repairs fail.
Notes: Review lesson objectives.

## Slide 16: Make-up of Concrete
Cement:
A binder that works in concrete to hold aggregate together
Aggregate:
The gravel or sand that gives the concrete mass (can vary in size)
Water:
Activates the cement to hold it all together
10-15%
60-75%
15-20%
+
+
The make-up or “recipe” of concrete can change based on desired outcomes, therefore many variations are possible.
For example, one could:
Increase water
Include additives (admixtures)
Use different sized aggregate
Concrete is a composite material of cement, aggregate, and water.
Notes: Before we begin discussing how to effectively evaluate and repair damaged concrete, it is important to understand how reinforced concrete works.
Concrete is a composite material comprised of three main elements: the cement, the aggregate, and the water.
Cement only accounts for about ten-to-fifteen percent of the total composite, depending on the application. The remaining bulk is aggregate. The water activates the cement as the binder and hydrates the concrete.
Sometimes these ratios change. There are a limitless number of “recipes” for concrete. Choosing the right one depends on a variety of factors. We will cover how to choose the best repair materials and methods in this course.
----------------------------------------
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
True or false: In its most basic form, concrete is comprised of water, cement, and aggregate.
True
False

## Slide 17: How Concrete Reacts Under Loading
Compression
Tension
Compression
4000 PSI
Tension
400 PSI
Concrete without reinforcement is strong in compression, but weak in tension.
Shortens
Lengthens
What can be done to combat this?
Notes: Concrete is strong in compression–this is one of the reasons it is used in columns and areas that carry heavy loads like roadways and flooring. However, it is weak in tension.
In this image, we can see that when a vertical slab of concrete is subjected to vertical gravity loads, it naturally wants to bow out of plane. The top of the concrete slab is experiencing compression and will shorten, but its integrity will not be compromised. When we examine the bottom of the slab, we can see it is experiencing tension. It has began to crack along the point that is most impacted by the gravity load.
What can be done to combat this?

## Slide 18
How Reinforced Concrete Acts Under Loading
Shortens
Lengthens
Compression
Tension
Concrete carries COMPRESSION loads
Steel carries TENSION loads
Concrete with reinforcement is strong in compression and tension.
Notes: Added reinforcement, such as a steel reinforcing bar (or rebar, as it is called in the field), along the bottom of the slab, can carry the tension load. The top of the slab will still be carrying the compression load, but since concrete is strong in compression, this part of the beam will not require reinforcement.

## Slide 19: Make-up of Reinforced Concrete
Reinforced concrete is a composite
Concrete carries compression strength
Reinforcing bar carries tension strength
Together, the reinforcing bar and the concrete create a composite that is strong in compression AND tension.
Notes: Reinforced concrete is considered a composite material. A composite material refers to materials made up from two or more materials with significantly different properties that, when combined, produce a material with characteristics different from the individual components.
Since this composite of steel reinforcing bar and concrete is strong in both compression and tension forces, it is ideal for a number of structural applications.

## Slide 20: Where is concrete used?
Because reinforced concrete is strong in both compression and tension, it is the most widely used building material in the world.
Concrete can be used for:
  Roadways
  Bridges
  Columns
  Foundations
  Parking structures
  Barriers
  …and many more applications
Notes: Concrete is one of the most widely used building materials because of its flexibility of design and versatility. It can be used in roadways, bridges, flooring, columns, and parking structures in addition to numerous other applications.

## Slide 21: Concrete Lifespan and Failure Modes
If well designed and regularly maintained, concrete could last up to 50 years
… but many factors decrease this lifespan, such as:
Corrosion of Embedded Rebar
Disintegration Mechanisms
  Exposure to aggressive chemicals
  Freeze-thaw disintegration cycles
  Alkali-aggregate reactions
  Sulfate attacks
  Erosion by cavitation or abrasion
Moisture/Thermal Effects
Load Effects
Unanticipated Disasters
  Tornados, earthquakes, hurricanes etc.
Improper Design or Construction
In this image, the concrete failed because the embedded metal reinforcing bar corroded
For more information on why concrete deteriorates, refer to our Deterioration course.
Notes: It is impossible to determine the lifespan of any placed concrete because there are so many factors that affect concrete’s performance. While some concrete can last for up to 50 years, other concrete may be subjected to damaging conditions and may only last a year or two before it begins to fail.
Factors that may lead to concrete deterioration include embedded rebar corrosion, disintegration mechanisms (such as aggressive chemicals), freeze-thaw cycles, abrasion, moisture effects, thermal effects, heavy loads the structure was not intended to carry, unanticipated disasters, or improper design or construction.
It can also be a combination of these things!
For more information on why concrete deteriorates, let participants know that there is also a “concrete deterioration” course that we offer as an online offering.

## Slide 22: What is the most common repair failure?
Chart: Most Common Repair Failures
| Corrosion | Cracking | Debonding | AAR | Other
Series 1 | 22 | 30 | 24 | 4 | 15
Repair failures are usually caused by:
the incorrect diagnosis of the original cause of the deterioration
the incorrect design of the repair or method of application
incorrect selection of material
poor workmanship
CON REP NET Network Newsletter No. 3." CON REP NET. N.p., May 2004. Web. June 2015.
All of these issues could have been prevented if the specifier or installer had known better!
Why do concrete repairs fail?
Alkali-Aggregate Reaction
Notes: As you can see from this chart, cracking is the most common mode of failure in repaired concrete. It is also usually the first indicator of a deeper problem. Cracking may be an indicator of corrosion, alkali-aggregate reaction, freeze-thaw disintegration, drying shrinkage, abrasion, or a variety of other issues.
There are a variety of reasons why concrete fails. Here we can see a few of the most common causes, including the incorrect diagnosis of the original cause of the deterioration, the incorrect design of the repair and method of application, incorrect selection of material or poor workmanship.
All of these causes of failure are fixable! Proper education can prevent these types of failures from happening.

## Slide 23: Repairing Concrete
The best way to fix deteriorated concrete is to completely start over.
But that’s not always feasible.
In this course, we’re going to look at the ways to repair existing concrete structures in order to prolong the service life.

## Slide 24: How effective are repairs?
HALF
of all concrete repairs fail within the five years of being placed.
Why is this?
The main reason repairs fail is because they are designed without assessing the cause of the damage.
Notes: Ask the audience: What percentage of concrete repairs are effective after 5 years?
Once a few people respond, reveal the correct answer.
Experts estimate that half of all concrete repairs fail within the first five years.
When you consider 1.) that repair materials are often stronger than the substrate they are replacing and 2.) that new concrete could last up to 50 years if properly placed and treated, it is obvious that repairs are not being effectively executed. As we just saw, many times, a repair is conducted without understanding what caused the concrete failure/deterioration in the first place!
Let’s look at an example.

## Slide 25: Example: Cracking
Corroding reinforcing steel bar
What caused this crack?
Cracks can be caused by a variety of issues, how we repair them depends on what caused the damage.
In this case, the crack was caused by the corrosion of the reinforcing bar.
Notes: Here we can see that this concrete was cracked, which is one of the most common concrete repair failure methods. Cracks can be caused by a variety of issues, ranging from impact loads, to corrosion of the embedded metal rebar.

## Slide 26: Example: Cracking
Corroding reinforcing steel bar
Cracks provide access for surface-introduced chlorides
Cracking and spalling of the concrete
What does “corrosion of reinforcing bar” mean?
Carbonation changes the pH of the concrete and therefore removes the passivity layer that protected the concrete.
Notes: When a reinforcing bar corrodes, the build-up of rust increases the volume of the bar. The concrete above the reinforcing bar cannot accommodate for this volume change so it cracks and eventually spalls off.
In this example, this concrete cracked because chlorides seeped through the concrete, reached the reinforcing bar, and corrosion of the steel rebar began.
The process of carbonation changed the pH of the concrete (from a more to a less alkaline environment) due to the interaction of water, atmospheric carbon dioxide, and the calcium hydroxide in the cement paste. Calcium hydroxide is a bi-product of the cement hydration process.
The lower pH causes the passivity layer around the rebar to diminish, which makes the concrete more conducive to setting up a corrosion cell.

## Slide 27: What does cracking show?
Cracks in concrete should be like a smoke alarm—an indicator of a larger problem that needs to be investigated.
“Something is wrong here! Investigate the issue!”
If the crack in the previous slide was not addressed, more serious spalling could occur and the concrete could reach its ultimate capacity and fail.
Notes: Concrete fails when it reaches its ultimate capacity, but this may not happen all at once. Often the first sign of distress in a concrete structure is tension cracks.
Think of these tension cracks as “smoke alarms” as they are often the first indicators that something is wrong and needs to be looked into.
If the crack in the previous slide was not addressed, more serious spalling could occur and the concrete could reach its ultimate capacity and fail.

## Slide 28: Example: Cracking
Because the underlying issue was not addressed…
What would happen if we just filled this crack with epoxy?
eventually, the repair will fail.
In fact, because the repair material is often stronger that the substrate, more cracks would form parallel to the area repaired with epoxy.
Notes: However, let’s say the person designing this repair did not investigate this issue. Instead of addressing the underlying corrosion of the reinforcing bar, they simply filled the crack with epoxy, using a gravity-feed method.
Ask the audience what they think will happen. After you have given the audience a change to answer, proceed.
The reinforcing bar will keep corroding. The repair will fail because the cause of the problem was not addressed.
In fact, because the repair material is often stronger that the substrate, more cracks would form parallel to the area repaired with epoxy. This creates more opportunities for chlorides or disintegrating agents to enter the concrete and access the reinforcing bar. The repair will have to be executed again, only this time, the surrounding concrete will need to be completely removed, the rebar will need to be cleaned, and new concrete will have to be laid. Although this is a more expensive repair than the epoxy repair first used, the epoxy repair was not a solution to the problem. The first repair was an entire waste. If the larger repair was done first, it would have provided a lasting solution and been altogether less expensive.

## Slide 29: The Process
Assess
1
Plan
2
Prepare
3
Execute
4
The underlying issue that caused the damaged must be determined prior to planning, preparing or executing the repair.
In this course, we will discuss how certain assessment, planning, preparation, and executing techniques will increase the likelihood of a lasting repair.
Notes: It is essential to assess the underlying cause of the damage before the repair is planned.
During a concrete repair, follow the four step process: Assess, Plan, Prepare, and Execute.
In this course, we will discuss how certain assessment, planning, preparation and executing techniques will increase the likelihood of a lasting repair.

## Slide 30: Assessing and Planning the Repair

## Slide 31: Assessing and Planning a Repair
In this lesson we will cover…
  The elements a Project Engineer should look for when assessing the concrete structure.
  Other repair requirements that should be taken into consideration when planning a repair.
  How proprietary repair materials can help provide effective solutions.
Notes: Review lesson objectives.

## Slide 32: Assessing the Repair
Assess
Sometimes the cause of the concrete failure is obvious
…sometimes it’s not.
The Project Engineer should conduct a thorough assessment of the damaged area in order to plan the best repair.
Notes: In order to identify the problem, the repair should first be assessed. In some cases the cause of the failure is obvious, such as fire damage. In other instances, the cause my only be determined by a careful evaluation.

## Slide 33: Assessing the Repair
How does the Project Engineer assess damaged concrete?
Visual Inspection
  Note observable characteristics of failure (moving or non-moving cracks?)
  Note environment
  Note potential loads
Collection of Data
  Original construction documents and drawings
  Soil reports
  Maintenance records
  Inspection reports
  Quality control documents
Testing and Examination
  Chloride and sulfate content test
  Alkalinity test
  Depth of carbonation test
  Crack movement test
Notes: First, a visual inspection should be conducted. Here the Project Engineer will note if there are any spalls, cracks, discoloration or any other observable characteristics of failed concrete. If there are cracks, they will determine if they are moving or non-moving. They will also observe the environment. If outside, they will consider what typical weathering elements is this structure subject to? Is the area damp? Is it subject to heavy loads? Traffic? Does the failure seem to be localized to the surface or does it go deeper?
Next, they will collect all data that pertains to the structure. This step in the process will include, but is not limited to, reviewing the original construction documents and drawings, soil reports, maintenance reports, inspection reports and documents related to the quality control of the materials, and mixes used in the original placement.
In the final phase of the assessment, some testing should be conducted. Based on evidence found in the visual and collection of data phases, the project engineer should have enough information to recognize which types of testing to conduct.
These evaluations can include chloride and sulfate content testing, alkalinity testing, depth of carbonation testing, and testing if cracks are moving or non-moving. The results of these test will help determine which repair material and placement method is appropriate for this repair.
There are many different methods for testing the damaged substrate. Refer to ICRI Technical Guidelines for more information on how to conduct various tests for evaluating existing concrete substrate.

## Slide 34: Identify the Cause
Many things can cause deterioration:
Carbonation
Fire
Overloading
Environmental pollution
Earthquake
Frost
Inadequate coverage of reinforcement
Corrosion of reinforcement
High water content
Aging
Plants or microorganisms
Oils
Acids
Poor workmanship
Deicing salts
Faulty design
Acids
Often it is not just one thing, but rather a
combination of these factors that causes deterioration.
Notes: After the assessment is completed, the Project Engineer should have a pretty good idea of what caused the failure.
Concrete deterioration is often not just caused by one thing. It is usually caused by a combination of these factors.

## Slide 35: Other Requirements
In addition to assessing what went wrong, there are other conditions that will affect how the Project Engineer plans the repair. The following should also be considered:
Owner Requirements:
Service Conditions
Application Conditions
Do they want an clean finish?
Do they want a quick turn around time?
What is their budget?
Load carrying requirements?
Exposure to gases/chemicals?
Moisture of the area?
Geometric size and configuration of repair?
Size and spacing of reinforcing bar?
Accessibility?
Notes: First the Project Engineer must ask him or herself, “What are the requirements of this repair?” In order to determine the scope of the repair, you will need to evaluate different categories of requirements.
Owner Requirements: One should especially take the owner requirements into consideration when planning which repair materials and methods to use for the job since they are the ones funding the project. Do they want an aesthetically pleasing finish? Are they concerned about a quick turn-around time? What is their budget?
Service Conditions: Service conditions refer to the elements the repair will be exposed to upon completion. Some examples of service conditions that would affect how a repair is planned: load carrying requirements, exposure to atmospheric gases/chemicals, moisture and temperature conditions
Application Conditions: Application conditions refer to the physical limitations of the repair. Some examples of application conditions that would affect how a repair is planned: Temperature, wind velocity at time of the repair (if exterior repair), geometric configuration of the repair, size and spacing of reinforcing bar
When selecting a repair material, remember that you want to match the material you use with what the damaged area needs. For example, you would use different repair materials on a non-structural driveway crack than you would for a basement wall that has honeycombed and is currently leaking.

## Slide 36: Planning the Repair
Is the repair structural or non-structural?
What are the owner requirements?
What is the environment like?
What is the desired turn-around time?
Is the crack delaminated?
Planning a repair will require the Project Engineer to take many things into account.
Inadequate planning can be the major cause of concrete repair failures.
Plan
Notes: Planning a repair will require the Project Engineer to take a variety of things into account.
Inadequate planning can be the major reason for concrete repair failures. If concrete fails mostly because of its environment and environmental factors were not taken into account when planning which materials and repair methods to use, the repair would not be successful.
In this section, we will look at what the Project Engineer will consider when selecting a repair material to increase the likelihood of a lasting repair. We will then move on to review the best way to apply these repair materials.

## Slide 37: Material Compatibility
Existing Substrate
Repair Material
Repair materials are inherently different than the existing substrate…
…but the goal is to match them as closely as possible.
Material incompatibility is a major cause of repair failures.
Notes: Selecting the correct material for an application is one of the most important parts of the repair process. Material incompatibility is a major cause of repair failures (ICRI 320.2R).
A repair will result in a composite material, comprised of the original concrete substrate, the bond area where the old and new material meet, and the repair material. The repair material will undoubtedly differ from the substrate in some way, but the goal is to match it as closely as possible so that it reacts similarly.
Compatibility is a balance of how the physical and chemical properties of the repair material and the substrate work together. Assessment of the proper repair materials must consider the behavior of the repair material in both cured and uncured states.

## Slide 38: Material Properties
For example, if you were fixing a hairline crack, you would need a repair material that was highly flowable.
Bond Strength—how strong is it?
Dimensional Behavior—how will it cure?
Durability—how will it behave over time?
Mechanical Properties—how does it react under certain loads?
Constructability—how easy is it to work with?
Material properties refer to the characteristics of the repair material:
Certain material properties are essential for certain repairs.
Notes: Let’s look at some desired properties of repair materials.
Bond strength typically is achieved by proper surface preparation and refers to how strong the bond is between the substrate and the newly placed repair material.
Dimension behavior refers to how the material will cure over time. This is an important property to consider as shrinkage is a major concern in repair materials. Although it may be difficult, selecting a repair material with minimal drying shrinkage will increase the likelihood of a lasting repair.
Durable repairs will retain the original, intended form and quality when exposed to its environment over time.
Mechanical properties refer the material’s ability to absorb and resist stresses that they are subjected to in their environment.
Constructability refers to how easy is it to work with the material? Constructability is also influenced by the owners operating requirements such as noise requirements, turn-around time, no tenant interference etc.
Most of the time, when the Project Engineer selects which properties are critical to the repair, it is a give-and-take relationship. Most likely, one property will have to be sacrificed in order to optimize another that may be more critical to the repair.

## Slide 39: Water to Cement Ratio
Look at what can happen over a 7 day period…
Chart: 
Low W/C Ratio | 6230
High W/C Ratio | 4677
More water less strength
The concrete with a higher water content had significantly less strength than the concrete with a lower water content.
Sometimes, when the concrete is not easily placeable, installers will just add more water.
Notes: Changing the proportions of the ingredients that make up concrete will affect how the concrete is placed and how it will cure. For example, on the jobsite, sometimes installers will add more water to make the material more flowable (and therefore easier to place). However, this means that more water will evaporate as the material cures, and will increase the likelihood of undesirable shrinkage.
Let’s look at an example of two different mixes with different water to cement ratios.
Based on this chart we can see that water with a lower water-cement ratio gained greater compressive strength in the same amount of time. This means that the less water you use during the placement of concrete or a repair material, the stronger the concrete will be.

## Slide 40: Water-Cement Ratio
  Increase curing and drying shrinkage
  Increase porosity
  Increase creep
  Reduce abrasion resistance
  Cause segregation
In addition, concrete with a high water to cement ratio can…
More water results in a higher risk of shrinkage cracks.
It is better to use a product which is designed to be placed at the desired consistency rather than add additional water. Admixtures can help with this.
Image from ICRI 320.2R-2009. Fig 3-5 Shrinkage cracks.
Notes: In addition to a decrease in strength and increase in shrinkage potential, excess water can also increase porosity (making it easier for chemicals to reach the rebar), increase creep, reduce the concrete’s ability to resist abrasion, and can cause segregation.
The bottom line is, it is better to use a product which is designed to be placed at the desired consistency rather than add additional water to try and change the consistency of the product. This will weaken the quality of the concrete.

## Slide 41: Admixtures
Certain desired material properties can be enhanced by the use of admixtures. Some examples of admixtures added include:
Accelerating Admixtures—increase set time (for cold weather)
Retarding Admixtures—decrease set time (for hot weather)
Water-Reducing Admixtures—reduce amount of water needed for placement
Shrinkage Compensating Admixtures—decrease shrinkage potential
Corrosion Inhibitors—protect against corrosive agents
Air-Entrained Concrete—protect against freeze-thaw cycle damage
Lithium-Based Admixtures—protect against alkali-silica reactivity
Notes: Admixtures, or additives, are incorporated into proprietary repair materials to enhance the concrete’s effectiveness, constructability, and durability.
Different admixtures are used depending on the properties we want to enhance.
An accelerating additive, for example, could be used in cold-weather applications in which the repair material typically takes a long time to set.
Air-entrained concrete can be used in areas that are subject to freeze-thaw cycles, thus reducing possible damage and delamination.
Some of these admixtures are known as water-reducers and help decrease the water-cement ratio without compromising workability during application.
While it may sound like a good idea to add many of these admixtures to combat different factors, it be best to keep the recipe as simple as possible.

## Slide 42: Proprietary Repair Materials
Admixtures
Enhance the desired material properties
=
Proprietary Repair Mortars
“Normal” Concrete
+
Proprietary repair materials already have admixtures included in their make up. The admixtures chosen for each proprietary repair mortar enhance the properties needed for particular jobs.

## Slide 43: Other Repair Materials
In addition, there are other materials that can be used in the repair process to increase strength and durability.
We’ll talk about these materials as they come up in the preparatory and execution phases of the repair, but note that they are selected by the Project Engineer prior to the actual date of the repair.

## Slide 44: Checkpoint Questions
Which of the following would be considered an owner requirements for a repair?
Smooth surface texture desired
Minimal UV exposure
Temperature average high of 90°F
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 45: Checkpoint Questions
Which of the following would be considered an owner requirements for a repair?
Smooth surface texture desired
Minimal UV exposure
Temperature average high of 90°F
Owner requirements are limitation of the repair as dictated by the owner/stakeholder. These can include aesthetic elements, time constraints, hours of work, etc.

## Slide 46: Checkpoint Questions
Which of the following would be considered a service condition for a repair?
Spacing of reinforcing bars 6” apart
Minimal live loads
Quick turn-around time

## Slide 47: Checkpoint Questions
Which of the following would be considered a service condition for a repair?
Spacing of reinforcing bars 6” apart
Minimal live loads
Quick turn-around time
Service conditions refer to the elements the repair will be exposed to upon completion. The live load the repaired structure will need to carry will dictate which types of materials should be used.

## Slide 48: Checkpoint Questions
Which of the following would be considered an application condition for a repair?
Minimal live loads
Repair thickness of 6” deep
Low moisture condition

## Slide 49: Checkpoint Questions
Which of the following would be considered an application condition for a repair?
Minimal live loads
Repair thickness of 6” deep
Low moisture condition
Application conditions refer to the physical limitations of the repair. The geometric configuration of the damage and other similar physical restraints will influence which materials and method of placement will be selected for a repair.

## Slide 50: Checkpoint Questions
Increasing the water-to-cement ration in a repair material will do all of the following things, except:
Increase porosity
Reduce abrasion resistance
Decrease drying shrinkage

## Slide 51: Checkpoint Questions
Increasing the water-to-cement ration in a repair material will do all of the following things, except:
Increase porosity
Reduce abrasion resistance
Decrease drying shrinkage
Increasing the water-to-cement ratio can increase drying shrinkage. It’s always best to use a product which is designed to be placed at the desired consistency instead of adding more water.

## Slide 52: Section Review
Be sure that the underlying cause of the damage was properly assessed prior to planning the repair.
Remember to use a repair material that not only fixes the issue, but also best suits the parameters of the application.
To review:

## Slide 53: Preparing For the Repair

## Slide 54: Preparing For a Repair
In this lesson we will cover…
  Jobsite safety requirements.
  How to properly remove delaminated concrete.
  How to prepare a concrete surface to increase the likelihood of a successful repair.
  Application techniques for primers and bonding agents.
Notes: Review lesson objectives.

## Slide 55: Preparing For the Repair
Prepare
“The repair is only as good as the surface preparation.”
–ACI 546R-14
Guide to Concrete Repair
Once the concrete has been properly assessed and the repair has been fully planned, it’s time to prepare for the repair.
First, we’ll look at how to prepare a concrete structure in which the concrete has delaminated.

## Slide 56: Trial Installation
“Trial installations are costly and time consuming, I don’t have the time or resources for that.”
This is probably the case in most jobs… and that’s okay!
While it’s a good idea to get familiar with the methods and materials selected for the repair, in smaller projects this may be an unnecessary step.
On large-scale, high-risk projects, a trial installation may be a good idea to evaluate if the repair will be effective.
Notes: Although it is not always feasible to do a trial installations, resources providing, it is a good idea to do a trial run of the repair on a small area in order to get familiar with how the repair materials will react with the substrate and with the placement method, particularly if it is new to the installer.
While we understand that trial installations are rarely done because of tight schedules funds or a variety of other reasons, resources permitting, a trial installation is a great way to increase understanding of how the repair will perform, especially on larger projects with significant investment.
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
In which of the following situations would it be important to conduct a trial installation?
A short-turn-around repair of a high-profile bridge
A horizontal spall repair on a residential street
A deteriorated column in a parking garage

## Slide 57: Preconstruction Meeting
Include all participating parties:
  Owner
  Engineer
  Contractor
  Materials Manufacturer
  Installer
This meeting should specifically address the parameters, means, methods, final appearance, timelines and timing restraints, accessibility of the repair, and materials necessary to meet the repair objective.
Make sure that everyone is on the same page so that there are no surprises!
Hold a preconstruction meeting.
Notes: A preconstruction meeting should be conducted. This ensures that everyone is on the same page moving forward with the project. All participating parties should be represented in the meeting. This includes, but is not limited to, the owner, engineer, contractor, materials manufacturer, and installer.
This meeting should specifically address the parameters, means, methods, final appearance, timelines and timing restraints, accessibility of the repair and which materials will be necessary to meet the repair objective (ACI RAP-1).
It is also a good idea to hold a preconstruction meeting for liability issues that may occur.

## Slide 58: Safety Considerations
MSDS
Job site safety practices should include…
Having material safety data sheets on-site at all times
Wearing PPE
Having eye-wash facilities accessible
Properly labeling and storing HAZMAT
Properly marking repair area
Notes: Job site safety practices should include having material safety data available on-site at all times, wearing proper protective clothing, having eye wash facilities accessible in the event of an emergency, wearing respirators when needed, securely storing and labeling hazardous materials, making sure there is proper ventilation in enclosed spaces, having necessary cleaning equipment on hand, and notifying the occupants of a repair process prior to beginning the repair, especially if there will be noise or airborne materials and/or debris.

## Slide 59: Locate Delaminated Concrete
1
OR
Chain Dragging
Hammer Sounding
These are two of the most common methods for locating delaminated concrete.
For more information on other methods, refer to
ACI 228.2R-13 Report on Nondestructive Test Methods for Evaluation of Concrete in Structures
ICRI 210.4 Guide for Nondestructive Evaluation (NDE)
Delaminated concrete should be located by hammer sounding or chain dragging.
If delamination has been found, the composite’s structural integrity is compromised.
Notes: First, delaminated concrete should be located. The two most popular methods of locating delaminated concrete are by chain dragging or hammer sounding. These are both non-destructive, methods.
Other methods for identifying delaminated concrete include:
Impact echo-testing (ASTM C1383)
Ground-penetrating radar (GPR) (ASTM D4788)
Infrared thermography typically accompanied by sounding by hammer tapping, chain draggig or impulse response.
For more information, refer to ACI 228.2R-13 “Report on Nondestructive Test Methods for Evaluation of Concrete in Structures” and ICRI 210.4-2009 “Guideline for Nondestructive Evaluation Methods for Condition Assessment, Repair, and Performance Monitoring of Concrete Structures”.

## Slide 60: Decision Point
2
After sounding a crack, was delamination found?
Yes
No
Delaminated concrete needs to be removed and replaced.
Concrete does not need to be removed and replaced.
Other repair methods should be considered.
2b
2a
Cracks caused by abrasion, overloading, shrinkage, or other non-corrosive means may not be accompanied by delaminated concrete.
Notes: Based on the findings of the sounding (or other delaminated concrete location means) a decision will need to be made. if the concrete is sounded and no delamination is present, the concrete does not have to be removed and replaced since delaminated concrete has already lost significant strength and will no longer perform as expected. Other repair methods can be considered depending on the nature of the damage. This being said, one still needs to determine the cause of the damage before planning the type of repair method. If delamination of the concrete surface was discovered, the deteriorated concrete will need to be removed, undercut, and replaced.

## Slide 61: Decision Point
2
For example:
If light honeycombing occurred without the presence of delamination, the surface could be re-profiled and new material could be added without major concrete removal.
No
Concrete does not need to be removed and replaced.
Other repair methods should be considered.
2a
After sounding a crack, was delamination found?
Notes: For example, if there was one long crack that had no delamination surrounding it, the crack could be filled without a full removal and repair of concrete. Similarly, if light honeycombing occurred without the presence of delaminated concrete, the surface could be re-profiled in order to accept the new material. In both instances, major concrete removal would not be necessary. This being said, always make sure to identify the cause of the issue (either cracks of honeycombing in these examples) before determining the repair method and strategy.
That being said, always make sure that the cause of the issue was identified before the repair materials and placement methods were selected.

## Slide 62: Decision Point Continued
“But if no delaminated concrete is found, why do I need to fix the crack?”
ALWAYS address the issue as soon as you can. This will save time, money, and labor in the long run.
REMEMBER:
  Cracks make it easier for deteriorating agents to access the concrete or reinforcing bar.
Notes: Some may think that cracks that are not associated with delaminated concrete do not need to be filled and are only an aesthetic concern. This is a false assumption.
As covered previously, cracks make it easier for deteriorating agents to access the concrete or reinforcing bar. If cracks are not sealed, these deteriorating agents (such as moisture, sulfates, de-icing salts, salt water, and other corrosive agents) can easily access the concrete and/or reinforcing bar which can lead to corrosion, alkali-aggregate reactions or freeze-thaw deterioration. Not only are these situation more devastating to the make-up of the concrete, they are much more costly and labor intensive to repair.
Fixing the situation as soon as it arises is always the best way to save time and money in the long run.

## Slide 63: Decision Point
If you sound a crack, and DO NOT FIND delaminated concrete around the area, you do not need to remove the concrete.
2a
Gravity-feed epoxy injection
Methyl-methacrylate flood-coating
Prepared cracks can be filled a low-viscosity repair material without removing the surrounding concrete.
We’ll cover how to properly repair a crack later in this course.
Notes: At this point, if no delamination is found, a full-depth repair may not be necessary. Cracks that occur from loading, abrasion, drying shrinkage or other non-corrosive means, may just be cracks, and not a symptom of a greater issue.
After cracks without surrounding delamination are properly prepared, they can be filled with a low-viscosity repair material that can seep into the crack and seal the concrete from deteriorating agents that could enter and cause further issues.
This kind of repair is often done when the crack is found in its early stages. If cracks like this are left for too long, more serious issues may arise as they could be subject to freeze-thaw cycles, corrosion, or heavy chemicals that could break down the concrete’s make-up.

## Slide 64: Remove Delaminated Concrete
2b
Use a 15 lb. chipping hammer to remove concrete
Chipping Hammer
If you sound a crack, and FIND delaminated concrete, you need to remove and replace the concrete and continue with the following steps in this section.
Common way to remove concrete:
Chipping hammers larger than 15 lb. could bruise good concrete!
Use with care.
After using a demolition hammer, check for micro-cracking of the substrate that could be caused by the hammer.
Notes: However, if delaminated concrete is found, you will follow a different set of steps. Remove the unsound concrete. There are many ways to remove unsound concrete and different applications require different methods. Let’s look at two common methods.
Typically, a fifteen-pound chipping hammer (sometimes called a demolition hammer) is used. Chipping hammers larger than fifteen pounds can potentially cause damage to reinforcement or could bruise good concrete. After using these hammers, be sure to sound the concrete again for micro-cracking of the substrate that could have been caused by the hammers.

## Slide 65: Remove Delaminated Concrete
2b
Uses water under high pressure directed against the surface to remove concrete.
Another common way to remove concrete uses hydrodemolition.
Advantages
Ideal for removing concrete around embedded rebar
Can be used to break up rust on the rebar if present
Disadvantages
Can be costly
Refer to ACI 546R-14 Guide to Concrete Repair for an in-depth explanation and assessment of alternative concrete removal methods. This guide also explores in which instances certain concrete removal methods would be preferred.
Notes: Other methods of concrete removal include hydrodemolition. This method removes delaminated concrete using highly pressurized water directed towards the delaminated concrete surface. This method is ideal for removing concrete around the embedded rebar as it can clear concrete away from underneath the embedded metal. It can also be used to break off rust, if present, that has formed on the reinforcing steel bar.
Refer to ACI 546R-14 Guide to Concrete Repair for an in-depth explanation and assessment of alternative concrete removal methods listed below. This guide also explores in which instances certain concrete removal methods would be preferred.
Some other methods to remove unsound concrete include:
Mechanical shearing
Stitch drilling
Impact methods
Boom mounted breakers
Scabblers
Needle scalers
Scarifiers
Milling methods
Explosive blasting
Presplitting methods
Hydraulic splitter
Water-pulse splitter
Expansive product agents
Refer to ACI 546R-14 “Guide to Concrete Repair” for an in-depth explanation and assessment of each of these concrete removal methods. This guide also explores in which instances certain concrete removal methods would be preferred.
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
True or false: In addition to removing concrete, hydrodemolition also can break up the rust on the rebar if present.
True
False

## Slide 66: Mark the Perimeter
3
Next, you will need to mark the perimeter of where you are going to remove the concrete.
You should mark the perimeter in the easiest possible configuration.
Notes: After removing the delaminated concrete, you should mark the perimeter of the area you intend to cut.

## Slide 67: Mark the Perimeter
3
INCORRECT
CORRECT
Let’s say this is a diagram of where the concrete has delaminated.
This would be the correct formation to cut.
Simple, rectangular layout
We don’t want to make the concrete “go around corners.” It will crack at these locations.
Notes: The perimeter should be kept as simple as possible, configured in rectangular or square shapes and edges.
Many may resist this and want to cut the perimeter as seen on the right so that they don’t have to remove and replace as much concrete. However, was you can see, highlighted in yellow, cracks will always occur at the weakest point.
If the repair was saw cut in this way, more cracks could have occurred around the repaired area and another repair would need to take place. All of that work would have been for nothing.
Remember, the most simple layout is the best. Concrete cannot go around corners, it will always crack.
You will inevitably have to remove some good concrete to obtain the correct, rectangular formation.

## Slide 68: Saw Cut the Perimeter
4
Do not cut the reinforcing bar!
Next, saw cut the perimeter.
After saw cutting, remove all concrete within the saw cut area. This means you will remove some sound concrete to ensure a simple, geometric configuration.
Notes: Once you have marked the perimeter in a clear, rectangular, geometric shape, saw cut the perimeter.
The saw cut should not be deeper than the cover over the reinforcement. Do not cut the reinforcing bar!
After saw cutting, remove the concrete within the saw cut area, using a small demolition hammer or hand-held hammer for more sensitive concrete remove. Remember, you will need to remove some sound concrete to ensure that you are making a geometric configuration.
Again, remember to take care not to bruise the substrate as you remove the concrete as this can cause more concrete delamination now the line.

## Slide 69: Undercut Reinforcing Bar
5
Undercut the rebar.
Undercut
90°
¾
Proper undercutting ensures that the entire rebar is covered in the new repair material.
Clearance under corroded rebar should be at least ¾″ (0.75) in.
“Concrete removal should continue around the reinforcing steel to create a minimum of 0.75 in. (19 mm) clearance to the surrounding concrete or 0.25 in. (6 mm) larger than the coarsest aggregate in the repair material.”
- p. 9, ACI 546R-14 Guide to Concrete Repair
Notes: If reinforcement is corroded, you must cut away the concrete underneath the rebar. The depth of the cut under the rebar should be at least three-fourths of an inch or one-fourth of an inch greater than the largest aggregate size in the repair material, whichever is greater.
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
How much should you undercut the rebar when conducting a structural repair?
1/4" or at least 1/4" greater than the largest aggregate size of the repair mixture, whichever is greater
1/2" or at least 1/4" greater than the largest aggregate size of the repair mixture, whichever is greater
3/4" or at least 1/4" greater than the largest aggregate size of the repair mixture, whichever is greater
1" or at least 1/4" greater than the largest aggregate size of the repair mixture, whichever is greater

## Slide 70: Undercut Reinforcing Bar
5
If corrosion caused significant loss of diameter, lap-splicing may be necessary.
Consult with the Project Engineer to determine the best method to address significant section loss of the reinforcing steel.
For more information on how to replace severely deteriorated rebar, refer to:
ICRI 310.1 R-2008 “Guide for Surface Preparation for the Repair of Deteriorated Concrete Resulting from Reinforcing Steel Corrosion”
Notes: If the rebar has been so heavily corroded that the diameter is significantly reduced, the repair should be reassessed by an engineer.
Adding supplemental reinforcing bar, also known as lap-splicing, is sometimes an adequate fix to restore strength to the structure.
If the engineer decides that the reinforcement needs to be removed entirely, consult ICRI 310.1 R-2008 “Guide for Surface Preparation for the Repair of Deteriorated Concrete Resulting from Reinforcing Steel Corrosion”.

## Slide 71: Prepare the Surface for the Repair Material
6
Proper surface preparation is essential for a good bond between the repair material and the existing substrate.
Verify that the substrate is correctly prepared.
We want the concrete to be:
Rough with teeth and open pores
Cleaned of laitance
Saturated-surface dry (SSD)
Notes: The concrete should be somewhat rough with teeth and open pores that will promote the interlocking of the substances as the repair material cures.
We also want to be sure that the concrete is cleaned free of laitance and any particles that could interfere with bonding.
The surface should also be saturated-surface dry (SSD), meaning that the surface is damp after cleaning. That being said, there should be no free-standing water that would interfere with the bonding of the repair material.

## Slide 72: Prepare the Surface for the Repair Material
These chips are given numeric values based on the size of their aggregate.
6
Concrete Surface Profile (CSP) chips can be used on the jobsite to verify that the substrate is correctly prepared.
Verify that the substrate is correctly prepared.
Notes: ICRI has created a concrete surface profile (CSP) chips for determining the surface profile necessary for various repair applications.
These chips, as seen in the example here, can be compared to the prepared substrate to help contractors and installers verify that the concrete substrate is properly prepared as specified based on the type of substrate being repaired.
The numbers of the chip refer to the size of the aggregate used in the concrete make-up.
These chips were originally created to allow the manufacturer of the material to specify the intended substrate.

## Slide 73: Surface Preparation/Cleaning Reinforcement
6
Abrasive blasting also cleans reinforcing steel
Abrasive blasting (sandblasting dry/wet)
Abrasive blasting (shot-blasting)
Wire brushing
Low-pressure water blasting (w/ abrasives)
Low-pressure water blasting (w/o abrasives)
Chemical cleaning
Acid etching
Proper surface preparation is critical can and be achieved by:
Verify that the substrate is correctly prepared.
Notes: Proper surface preparation is critical and can be achieved with abrasive blasting, as seen here, or with shot blasting, water blasting, wire brushing or using a variety of other cleaning methods.
Abrasive blasting is commonly used to both clean reinforcing steel and clean and profile concrete surfaces in preparation for the repair materials.

## Slide 74: Verify That All Delaminated Concrete Has Been Removed
7
Hammer sound or chain drag prepared area again to ensure that all delaminated concrete has been removed.
Notes: After preparing the surface you should again verify that all delaminated concrete is removed. This can be done by hammer sounding or chain dragging again, or using other delaminated concrete identification methods outlined in ACI 228.2R-13 and ICRI 210.4 will provide more in-depth information for testing delamination of concrete.

## Slide 75: Apply Primers
8
Apply the repair material (rebar primer)
The step “applying the repair material” has many parts. First, if deemed necessary, the exposed reinforcing bar can be coated with a primer to increase its protection against corrosive agents.
primer to protect reinforcing bar
Substrate undercut at least ¾″
in order to properly coat full circumference of the rebar.
Rebar was undercut, and cleaned of rust and corrosion prior to application of primer.
Undercut
90°
¾
Notes: If deterioration was caused by corrosion of the metal reinforcing bar, it may make sense to provide extra protection over the rebar in order to prevent this from happening again.
Primers are coatings on reinforcement that make it more difficult for corrosive agents to reach the rebar.
Zinc-rich primers, for example, are sacrificial coatings. Because zinc is a less noble metal than steel, when the corrosive elements come into contact with the rebar, the zinc coating will corrode instead of the reinforcement, therefore the strength of the structure is not compromised.
Zinc coatings are particularly ideal in areas where corrosive agents are expected (e.g., chemical plants or marine environments).

## Slide 76: Apply Primers
8
Apply the repair material (rebar primer)
Zinc-rich primers are sacrificial coatings.
This means that, when the rebar is exposed to corrosive elements, the primer will corrode first in place of the steel. This is because zinc is a less noble metal than steel.
Notes: Zinc-rich primers, for example, are sacrificial coatings. Because zinc is a less noble metal than steel, when the corrosive elements come into contact with the rebar, the zinc coating will corrode instead of the reinforcement, therefore the strength of the structure is not compromised.
Zinc coatings are particularly ideal in areas where corrosive agents are expected (e.g., chemical plants or marine environments).
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
How does a zinc-rich primer work?
When corrosive agents come into contact with the coated reinforcing bar, the coating will corrode instead of the reinforcing bar because zinc is a less noble metal
When corrosive agents come into contact with the coated reinforcing bar, the coating will corrode instead of the reinforcing bar because zinc is a more noble metal
When corrosive agents come into contact with the coated reinforcing bar, because zinc is a more noble metal, the coating will deflect corrosion and no part of the composite will experience damage

## Slide 77: What happens if you don’t undercut the rebar?
It is critical to coat entire circumference of rebar with primer, otherwise other sections of rebar will experience accelerated corrosion rates.
Zinc Primer
Steel Rebar
Original Substrate
Repair Material
Area that has corroded away!
No zinc primer
Since zinc primer was not applied under the rebar, not only was the steel not protected, it also experienced accelerated corrosion rates!
No Zinc Primer
INCORRECT APPLICATION OF REBAR PRIMER
8
Apply the repair material (rebar primer)
Notes: After the reinforcing bar is completely exposed with at least three-fourths of an inch undercut beneath the rebar, the primer should be applied around the entire circumference of the rebar. If you do not completely coat the entire rebar, the corrosive agents will attach a different part of the steel with more intensity.
In this example, the zinc coating did not cover the complete circumference of the steel rebar. The corroding agents attacked the steel with more intensity and eventually, just the zinc coating remained, the steel completely rusted away!
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
How does a zinc-rich primer work?
When corrosive agents come into contact with the coated reinforcing bar, the coating will corrode instead of the reinforcing bar because zinc is a less noble metal
When corrosive agents come into contact with the coated reinforcing bar, the coating will corrode instead of the reinforcing bar because zinc is a more noble metal
When corrosive agents come into contact with the coated reinforcing bar, because zinc is a more noble metal, the coating will deflect corrosion and no part of the composite will experience damage

## Slide 78: Apply Bonding Agents (If Desired)
8
Apply the repair material (bonding agent)
Some repairs fail because of the inadequate bonding of the repair material at the bond area.
Bonding Agents
Can be applied to prime the substrate to better receive the repair material
Notes: Some repairs fail because of inadequate bonding of the repair material to the substrate. This site is called the bond area.
Bonding agents that can prime the substrate to better receive the repair material.

## Slide 79: Apply Bonding Agents (If Desired)
8
Apply the repair material (bonding agent)
If using a bonding agent, it is essential to apply the repair material while the bonding agent is still tacky.
We want the bonding agent and the repair material to dry together.
WET on WET!
Fully coat the edges
Notes: A bonding agent should be applied after surface preparation is complete and before the repair material is placed. It is important that the edges are fully coated.
If you decide to use a bonding agent, remember that you should apply the repair material while the bonding agent while it is still tacky. Do not wait for the bonding agent to dry before applying your repair material—if you do so this could create a bond break instead. We want the bonding agent and the repair material to dry together in order to form a strong bond.

## Slide 80: Apply Bonding Agents (If Desired)
The effectiveness of bonding agents have been disputed in the field. Often, vigorously scrubbing the repair mortar into the prepared, open-pore substrate will achieve the same thing as a bonding agent.
This is known as a “scrub coat”
Here, we can see a close up of the open pore substrate accepting the repair material.
8
Apply the repair material (bonding agent)
The Debate About Bonding Agents:
Notes: Note that the effectiveness of bonding agents have been disputed in the field. Some say that bonding agents are just “one more thing to go wrong” with the repair and “one more thing to buy.” Research has shown that a good “scrub coat” can often be just as effective as a bonding agent, so if the Project Engineer is looking to decrease the costs of the repair, he or she may consider cutting the bonding agent.

## Slide 81: Now what?
In the next section, we will examine the different application methods that can be used for a structural repair in which the concrete needs to be removed and replaced.
= Apply the repair material
8

## Slide 82: Checkpoint Questions
Which of the following correctly describes a properly prepared concrete surface that is ready to accept the repair material?
The surface is rough with teeth and open pores.
The surface has been ground smooth and is slightly damp.
The surface has already been coated with a bonding agent that has been left to dry overnight
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 83: Checkpoint Questions
Which of the following correctly describes a properly prepared concrete surface that is ready to accept the repair material?
The surface is rough with teeth and open pores.
The surface has been ground smooth and is slightly damp.
The surface has already been coated with a bonding agent that has been left to dry overnight
Although the surface should be SSD, we want to substrate to have “teeth” to grip onto the new material. Also, if using a bonding agent, the repair material should be applied while the bonding agent is still tacky so that the material and the bonding agent dry together.
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 84: Checkpoint Questions
What should you do if you come across a reinforcing bar that has corroded so significantly that its diameter has decreased?
Remove and replace the reinforcing bar.
Clean off rust from reinforcing bar and coat with primer.
Consult the Project Engineer.
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 85: Checkpoint Questions
What should you do if you come across a reinforcing bar that has corroded so significantly that its diameter has decreased?
Remove and replace the reinforcing bar.
Clean off rust from reinforcing bar and coat with primer.
Consult the Project Engineer.
You should consult the Project Engineer whenever there is a question of structural integrity. If the diameter has significantly decreased, lap splicing may be necessary.
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 86: Checkpoint Questions
True or False. If you sound a concrete crack and find delamination, the concrete will need to be removed and replaced.
  True
  False
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 87: Checkpoint Questions
True or False. If you sound a concrete crack and find delamination, the concrete will need to be removed and replaced.
  True
  False
Delaminated concrete needs to be removed and replaced. If you were to fill the crack without removing the delaminated concrete, the issue would not be addressed and the concrete would continue to deteriorate.
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 88: Section Review
Proper surface preparation dramatically increases the chances of a successful, lasting repair.
Be sure to sound for delamination and ensure that the substrate is rough with open pores so that it can grip onto the new, repair material.
To review:

## Slide 89: Executing the Repair

## Slide 90: Execute the Repair
In this lesson we will cover…
  Application methods for replacing concrete.
  Steps and considerations at each step in the application process.
  Advantages and disadvantages of each application method.
  Materials and methods for fixing a crack that is not accompanied by delaminated concrete.
Notes: Review lesson objectives.

## Slide 91: Executing the Repair
Execute
Once the surface is properly prepared, it is time to apply the repair material.
There are many different methods to do this. The method selected will not only need to fix the issue, but also be feasible for the constraints of the repair.

## Slide 92: Methods for Replacement of Delaminated Concrete
The next slides will provide an overview of repair application methods.
Each overview will include:
A general overview
A step-by-step guide of the application
Advantages and disadvantages of the method
Each of the repair methods covered has an associated ACI Repair Application Procedure (RAP) These are available as an online download from ACI.
Bulletin
RAP
Notes: Each of repair methods covered has an associated ACI Repair Application Procedure (RAP) These are available as an online download from ACI.

## Slide 93: Reprofiling Application
Reprofiling Application
Trowel-applied method seeks to reprofile, or level out a surface.
Best Application: Surface restorations when reinforcing steel is not encountered.
Material Requirements: fine-grained material that can be worked into a ball. It should have non-sag properties so that it can stay in place for the life of the repair.
Next, let’s look at the steps in this repair…
Bulletin
RAP-10
Notes: The primary purpose of this repair is to correct surface deficiencies and provide the intended design surface. These deficiencies can include nonmoving hairline or plastic shrinkage cracks, small or shallow surface air voids, honeycombs, or rock pockets. More often than not, this is done for aesthetic purposes.

## Slide 94: Reprofiling Application
Surface must be free of bond-inhibiting materials such as dust and laitance. Depending on the material, high-pressure, water-blasting, sand-blasting, etc. may be needed to ensure clean surface with open pores.
1
Steps in process:
Bulletin
RAP-10

## Slide 95: Reprofiling Application
Properly mix repair materials as specified by manufacturer. Material should be easily formed into a ball.
2
Steps in process:
Bulletin
RAP-10

## Slide 96: Reprofiling Application
Using force, press the repair material into the cavity using a trowel. Repair material is pressed into the substrate to develop intimate contact without voids. A second coating of the material may be required to provide adequate smoothness.
Hold trowel tight to surface to force material into voids and bugholes.
Strike off excess material.
3
Steps in process:
Bulletin
RAP-10

## Slide 97: Reprofiling Application
Advantages:
Can be used in vertical and overhead repairs
No formwork necessary
Less equipment is needed than in other repairs
Disadvantages:
Only ideal for areas where reinforced steel is not encountered
Success of repair is dependent on the laborer
Reprofiling Application: Things to Consider
Bulletin
RAP-10

## Slide 98: Hand-Applied (Dry Pack) Application
Hand-Applied (Dry Pack) Application
Hand-applying mortar and then packing it into the cavity is sometimes known as “dry-packing.”
Best Application: thin or cosmetic repairs for vertical or overhead locations.
Material Requirements: mortars that can be molded into a ball without sagging.
Bulletin
RAP-6
Notes: Hand application repairs are ideal in thin repairs that are cosmetic in nature. Although they can be used in structural repairs, in which repair material must be consolidated around the reinforcing bar (as seen in this image) opinions about the effectiveness of this technique vary. Some recommend that repairs encompassing the reinforcing bar should only use pressurized methods (meaning in a form-and-pour/pump method or shotcrete method, etc.) in order to ensure that the rebar is completely encapsulated without air pockets.
However, because the hand application method is simple, inexpensive, and does not require a variety of equipment, it is favored in many instances. Just remember to consider other methods when repairing around reinforcing bar as hand application will most likely not deliver the best results.
Next, let’s look at the steps in this repair…

## Slide 99: Hand-Applied (Dry Pack) Application
Remove unsound concrete and prepare using the method covered earlier. Ensure that surface is SSD (saturate-surface dry) with no standing water. Note that an SSD surface is not recommended when a polymer bonding agent is used.
1
Steps in process:
Bulletin
RAP-6
Notes: For more information refer to the RAP (Repair Application Procedure) 6 on Vertical and Overhead Spall Repair by Hand Application.

## Slide 100: Hand-Applied (Dry Pack) Application
Mix the material following the manufacturer’s recommendations. Material should be easily formed into a ball. Scrub a thin bond coat of the repair mortar into the SSD substrate—this will take the place of a bonding agent.
2
Steps in process:
Bulletin
RAP-6
Notes: It is very important to ensure that in every application, full bags of the product are mixed. This is because, as we learned earlier, proprietary repair materials are concrete with admixtures incorporated into them. Often these admixtures are added to the bag without the bag being thoroughly mixed. More of the admixture may be present at the bottom of the bag than at the top of the bag. Think about how when you are baking, you want to make sure to sift flour and baking powder together before you add the wet materials. It is the same with the ingredients in a concrete repair material.
For more information refer to the RAP (Repair Application Procedure) 6 on Vertical and Overhead Spall Repair by Hand Application.

## Slide 101: Hand-Applied (Dry Pack) Application
Apply the material with adequate pressure before the bond coat dries. Be sure to thoroughly consolidate the repair material into the corners and around any exposed reinforcement.
3
Steps in process:
May not be recommended in situations that include placing material around the reinforcing bar.
Bulletin
RAP-6
Notes: Although this type of repair method can be used in structural repairs that include the rebar, some guidelines recommend against this, saying that only pressurized methods should be used for structural repairs to ensure that the rebar is completely encapsulated at that the repair material is completely consolidated.
For more information refer to the RAP (Repair Application Procedure) 6 on Vertical and Overhead Spall Repair by Hand Application.

## Slide 102: Hand-Applied (Dry Pack) Application
Finish and cure the repair.
4
Steps in process:
Bulletin
RAP-6
Curing methods are outlined in ACI 3048R Guide to Curing Concrete.
Curing compounds are sprayed or rolled directly onto the finished surface immediately following the repair and will eventually dissipate after set amount of time without staining.
Notes: Curing compounds are sprayed or rolled directly onto the finished surface immediately following the repair and will eventually dissipate after set amount of time without staining. Other curing methods include wet wrapping the concrete so that it protects against premature drying or occasionally wetting the concrete surface.
For more information about curing methods, refer to ACI 3048R Guide to Curing Concrete.
For more information refer to the RAP (Repair Application Procedure) 6 on Vertical and Overhead Spall Repair by Hand Application.

## Slide 103: Hand-Applied (Dry Pack) Application
Advantages:
Can be used in vertical and overhead repairs.
Less expensive than other methods.
Less equipment is needed than in other methods.
Ideal for thin, cosmetic repairs.
Disadvantages:
Can be difficult to consolidate around reinforcing bar.
Success of repair is dependent on laborer.
Hand-Applied (Dry Pack) Application: Things to Consider
Bulletin
RAP-6
Notes: Note that this repair is particularly dependent on the skill of the installer. Because if this, with this type of placement method, it may be a good idea to conduct a small, trial installation, to ensure that the installers are familiar with how to properly place the material.

## Slide 104: Spall Repair of Horizontal Surfaces
Spall Repair of Horizontal Surfaces
Repair material is poured into open, properly prepared cavity.
Best Application: horizontal repairs where no framework is required.
Material Requirements: cast-in-place concrete with low shrinkage and a low water-to-cement ratio.
Bulletin
RAP-7
Notes: Refer to the Repair Application Procedure bulletin 7 published by the American Concrete Institute (ACI) for more details on executing this repair. Next, let’s look at the steps in this repair…

## Slide 105: Spall Repair of Horizontal Surfaces
Clean rebar and prepare surface.
1
Steps in process:
Bulletin
RAP-7
Notes: Remove unsound concrete and prepare in method covered earlier. Ensure that surface is SSD (saturate-surface dry) with no standing water. Use of bonding agent is optional.

## Slide 106: Spall Repair of Horizontal Surfaces
Place repair material into the cavity. Consolidate repair material.
2
Steps in process:
Bulletin
RAP-7
Be sure to evenly distribute and consolidate poured repair material to all corners.
Notes: After properly mixing, based on the manufacturer’s instructions, place the repair material into the prepared cavity. This can be achieved by pouring, as seen here, or through a pumpline.
Unlike shotcrete or form-and-pump applications that are self-consolidating, spall repairs or form-and-pour repairs will need the concrete to be consolidated to ensure that there are no air pockets in the poured material. This can be done using a vibrator as seen here.
In this image, you can see that the installer is pouring towards the middle/right of the repair area. He will need to take care to evenly spread out and consolidate the material over the entire area.

## Slide 107: Spall Repair of Horizontal Surfaces
Strike off and float the repaired surface. Trowel or broom the surface flat. Finish and cure with a curing compound to protect from early drying shrinkage.
3
Steps in process:
Bulletin
RAP-7
Curing methods are outlined in ACI 3048R Guide to Curing Concrete.

## Slide 108: Spall Repair of Horizontal Surfaces
Advantages:
Common on elevated or on-grade slabs.
Low cost (does not require expensive labor or intensive formwork).
Disadvantages:
Laborer needs to ensure proper spacing and consolidation of repair material, particularly at the corners.
Curing compounds may be needed.
Spall Repair for Horizontal Surfaces: Things to Consider
Bulletin
RAP-7
Notes: Horizontal surface repair is common on elevated or on-grade slabs. This repair does not require expensive and labor intensive formwork as the parameters of the repair are outlined by the saw-cut perimeter. Although this seems like a simple repair, there are many things that could potentially go wrong. It’s critical to properly prepare the surface prior to placing the repair material. Also the installer needs to ensure that the repair material is evenly spread out in the cavity, particularly at the corners and is consolidated to ensure that there are no air pockets as these pockets can provide a pathway for disintegrating agents.

## Slide 109: Form-and-Pour Application
Form-and-Pour Application
Formwork is erected, repair materials are poured into the cavity and consolidated with a vibrator.
Best Application: columns, walls, and exterior slabs.
Material Requirements: castable concrete, or mortar, with proper bond properties, low shrinkage, low water-to-cement ratio and is highly flowable.
Bulletin
RAP-4
Notes: In form-and-pour applications, formwork is erected and the repair material is poured inside. When selecting a material for this repair, placeability is the primary consideration. Consolidation is also done with vibration of rodding. A trial installation is highly recommended for this type of repair.
Refer to the Repair Application Procedure bulletin 4 published by the American Concrete Institute (ACI) for more details on executing this repair.
Next, let’s look at the steps in this repair…

## Slide 110: Form-and-Pour Application
After properly preparing the surface, erect the formwork.
1
Steps in process:
Bulletin
RAP-4
Note: It is critical that the formwork is designed and erected so that there is a way for the air to get out as the material is poured. This precaution decreases the chances of air pockets in the finished repair.
Notes: In the form and pour technique, after the delaminated concrete is removed and prepared (as we covered previously in steps 1-7), formwork is placed around the cavity. It is critical that the formwork is designed so that there is a way for the air to get out as the material is poured into place. This precaution eliminates the chances of air pockets in the finished repair.
Refer to the Repair Application Procedure bulletin 4 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 111: Form-and-Pour Application
After properly mixing, based on manufacturer’s recommendations, pour the repair material into the prepared cavity. Use vibrators to consolidate the repair material to ensure that there are no air pockets.
2
Steps in process:
Bulletin
RAP-4
Notes: Refer to the Repair Application Procedure bulletin 4 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 112: Form-and-Pour Application
Formwork is left on while the repair material cures. After the repair material has cured, the formwork is removed and a curing compound may be added to ensure that the material develops its full strength.
3
Steps in process:
Bulletin
RAP-4
Curing compounds may be applied to protect the repair from premature drying shrinkage.
Curing methods are outlined in ACI 3048R Guide to Curing Concrete.
Notes: Refer to the Repair Application Procedure bulletin 4 published by the American Concrete Institute (ACI) for more details on executing this repair.
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
True or false: Both curing compounds and surface treatments are types of coatings.
True
False

## Slide 113: Form-and-Pour Application
Advantages:
Many different materials can be used.
Repair material can be placed around reinforcement.
No potential sagging of materials.
Formwork prevents against early drying which could lead to undesirable cracking.
Disadvantages:
Formwork can be expensive to install and erect, especially in areas that are tricky to get to.
Formwork is more labor intensive.
Poured repair material will still need to be consolidated to ensure that there are no air pockets behind the formwork.
Form-and-Pour Repair: Things to Consider
Bulletin
RAP-4
Notes: Although many different types of repair materials can be used in this repair, the main limitation is that the building of the formwork makes the installation much more labor intensive than other alternative placement methods such as shotcrete or hand application.

## Slide 114: Form-and-Pump Application
Form-and-Pump Application
Formwork is erected. Repair materials are pumped into the cavity via concrete line until cavity is filled and pressurized.
Best Application: overhead and vertical repairs where congested reinforcement is present.
Material Requirements: pumpable, flowable, self-bonding, with aggregate size compatible with size of cavity and space between bars.
Bulletin
RAP-5
Notes: This method of placement is primarily used on vertical surfaces, such as walls or columns. This placement method can also be done as a “full-depth” repair in which an entire piece of concrete needs to be removed and replaced. In this situation, formwork (also sometimes known as shoring) will be erected on both sides of the beam or member and then the repair material is pumped into place. Not that the Project Engineer should take special precautions to ensure that the integrity of the structure is not compromise during the placement and curing process.
Next, let’s look at the steps in this repair…
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
Which of the following application methods is self-consolidating?
Form and Pour
Form and Pump
Spall Repair of Horizontal Surfaces
Hand Applied

## Slide 115: Form-and-Pump Application
After properly preparing the surface, erect the formwork.
1
Steps in process:
Bulletin
RAP-5
Be sure to leave a space to let entrapped air escape so that there are no air pockets in the final repair.
Notes: In the form and pump repair, the formwork is erected and then a pump is hooked up to the open cavity. The repair material is then pumped under pressure to fill the cavity. In this application, it is very important to leave a place for air to get out while the repair material is being pumped, otherwise, air pockets could occur in the repair.
Refer to the Repair Application Procedure bulletin 5 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 116: Form-and-Pump Application
Attach pumpline to formwork and begin pumping repair material. The pressurization from the pump consolidates the repair material as it is placed.
2
Steps in process:
Bulletin
RAP-5
Notes: Refer to the Repair Application Procedure bulletin 5 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 117: Form-and-Pump Application
Continue pumping repair material until entire cavity is filled. Shut off and remove pumpline.
3
Steps in process:
Bulletin
RAP-5
Notes: Refer to the Repair Application Procedure bulletin 5 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 118: Form-and-Pump Application
After concrete is allowed to cure for a prescribed time, the formwork is removed and curing compounds are either rolled on or spray-applied to protect the repair material from drying shrinkage.
4
Steps in process:
Bulletin
RAP-5
Notes: After the area has properly cured, remove the formwork and the surface is profiled. If necessary a curing compound can me added to aid the curing process or protective coatings can be added afterwards to ensure a lasting repair.
Refer to the Repair Application Procedure bulletin 5 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 119: Form-and-Pump Application
Advantages:
Placement not limited to thickness of repair.
Repair materials are pre-mixed.
No potential sagging of materials.
Formwork prevents against early drying while curing that can result in cracking.
Pressurization consolidates material around rebar.
Disadvantages:
Formwork can be expensive to install and erect, especially in areas that are tricky to get to.
Formwork is more labor intensive.
Form-and-Pump Repair: Things to Consider
Similar disadvantages to the form-and-pour application.
Bulletin
RAP-5
Notes: For this repair, sagging or dropouts of freshly placed materials aren’t an issue because all materials are supported by the formwork during the placement and curing process.
This placement method is ideal for structural repairs because the repair material is consolidated upon placement.
Because the repair material is tightly paced under pressure, this method may be ideal when the reinforcing bar is tightly packed and other placement methods may prove difficult to adequately consolidate around the rebar.
That being said, the formwork can also be expensive and time consuming to erect. The equipment is also costly and may require a more specialized installer.
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
Which of the following application methods is self-consolidating?
Form and Pour
Form and Pump
Spall Repair of Horizontal Surfaces
Hand Applied

## Slide 120: Preplaced Aggregate Application
Pre-Placed Aggregate Application
Formwork is erected. Gap-graded aggregate is placed into cavity and then grout is pumped until all voids are filled and pressurized.
Best Application: vertical/overhead applications where extremely low shrinkage of repair material is required.
Material Requirements: gap-graded aggregate, pumpable grout, self-bonding cement or binder.
Bulletin
RAP-9
Notes: Erecting formwork is already relatively costly and labor intensive. Since this application can be used for underwater repairs, creating this formwork can be even more costly and more labor intensive than if it were a simple form-and-pour. However, because this application method can decrease potential shrinkage by 50-100% it is often worth the added cost of having skilled laborers.
Refer to the Repair Application Procedure bulletin 9 published by the American Concrete Institute (ACI) for more details on executing this repair.
Next, let’s look at the steps in this repair…
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
Out of the following options, which repair application would most likely be the most expensive?
Pre-placed aggregate
Hand applied (dry pack)
Spall Repair of Horizontal Surfaces

## Slide 121: Preplaced Aggregate Application
Create formwork. Note that this application can be used in underwater repairs so this formwork may be erected underwater.
1
Steps in process:
Bulletin
RAP-9
Notes: Refer to the Repair Application Procedure bulletin 9 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 122: Preplaced Aggregate Application
Place the aggregate. Be sure to use gap-graded aggregate for this application so that grout can move around aggregate and fill voids.
2
Steps in process:
Bulletin
RAP-9
Type of aggregate to be used is specified in ACI 304.1R Guide for the Use of Preplaced Aggregate Concrete for Structural and Mass Concrete Applications.
Notes: In this application, the aggregate is placed first and then grout is pumped around the aggregate, filling the spaces between them. Since the aggregate is already tightly packed it ensures uniform distribution of the aggregate. It also can reduce potential shrinkage as often less binder is needed.
Be sure to use gap-graded aggregate for this repair so that the highly flowable grout can penetrate the packed aggregate and fill the voids.
Refer to the Repair Application Procedure bulletin 9 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 123: Preplaced Aggregate Application
Pump the grout into the cavity filled with aggregate. Start pumping at bottom of the placed aggregate. When port no longer accepts grout, move to port above until entire cavity is filled. After curing, formwork is removed.
3
Steps in process:
Bulletin
RAP-9
External form and pressurized grout placement will consolidate the repair materials as it is pumped.
Notes: The grout is then pumped into the cavity starting at the lowest pump. It is pumped until the binder begins to come out of the port above. The bottom port is then sealed and the pump is moved up to the port above. This is continued until the top pump no longer can accept any more of the binder. Like the form-and-pump application and any other method that installs the repair material under pressure, the repair material does not need to be consolidated after it is placed as the pressurized placement self-consolidates the concrete. After curing, the formwork is removed.
Refer to the Repair Application Procedure bulletin 9 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 124: Preplaced Aggregate Application
Preplaced Aggregate Application: Things to Consider
Advantages:
Can be used for underwater repairs.
Shrinkage can be reduced by 50-100%.
Aggregate is uniformly distributed.
Aggregate can be placed in “hard-to-get” locations.
Disadvantages:
Formwork can be expensive to install and erect especially in areas that are tricky to get to, such as underwater repairs.
Formwork is more labor intensive.
Proper proportioning of the structural grout mixture is necessary.
Bulletin
RAP-9
Most preplaced aggregate grouts are prepackaged with additives made specifically for this application.
Notes: In the pre-placed aggregate method, coarse aggregate is placed in a form and later grout is pumped in the cavity to fill around the voids of the aggregate under pressure. Most pre-placed aggregate grouts are prepackaged with additives made specifically for this application. This repair has many advantages, the greatest of which is that it can be placed underwater. Also, because the aggregate is already tightly packed, less cement/grout is used which therefore decreases possible shrinkage.
As with other repairs that use formwork, the set-up and prepwork can make this repair very costly.
Refer to the Repair Application Procedure bulletin 9 published by the American Concrete Institute (ACI) for more details on executing this repair.
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
Out of the following options, which repair application would most likely be the most expensive?
Pre-placed aggregate
Hand applied (dry pack)
Spall Repair of Horizontal Surfaces

## Slide 125: Shotcrete Application
Shotcrete Application
There are two types of shotcrete applications: dry-mix and wet-mix shotcrete.
Dry-mix: water and admixtures, if any, are introduced at the spray nozzle, just before the repair material is sprayed. It is more ideal for deeper applications and may produce more rebound.
Wet-mix: powder is mixed with water first and then sprayed. This method is more ideal for shallow repairs and offers less rebound.
Bulletin
RAP-12
Notes: Shotcrete applications are among the most economical and effective methods to repair concrete. Although other repair application methods that are self-consolidating require formwork, shotcrete does not. Therefore it is often used when forming requirements are too difficult or too expensive.
There are two types of shotcrete applications.
Dry process and wet process concrete. Each have their advantages.
With dry-process shotcrete, the powder only interacts with the water at the nozzle. This types of shotcrete is ideal for deeper applications because the material is stiffer. It also offers faster set times.
In wet-process shotcrete the powder is mixed with the water before the repair is started. The material is then sprayed into the cavity. This is advantageous because it produces less rebound and less mess, and is better suited for shallow repairs.
Refer to the Repair Application Procedure bulletin 12 published by the American Concrete Institute (ACI) for more details on executing this repair.

## Slide 126: Shotcrete Application
Dry-Mix vs. Wet-Mix Shotcrete
Next, let’s look at the steps in a shotcrete repair…
Bulletin
RAP-12
Dry-Mix Applications: material is dry and then meets water at the exit nozzle and then is propelled using compressed air onto prepared concrete surface.
Material Requirements: well-graded aggregate with necessary binders.
Wet-Mix Applications: pre-mixed repair material is propelled using compressed air onto the prepared concrete surface.
Material Requirements: pumpable, low-clump mixture which does not sag upon impact on the prepared substrate.
Notes: Dry-Mix Applications: Repair material is placed dry or slightly damp into shotcrete machine and mixed with compressed air.
Mixture is transported via hose to exit nozzle where water and admixtures are introduced. The ingredients are propelled onto the prepared surface and are consolidated by the force of the compressed air.
Material Requirements: well-graded aggregate with necessary binders. Admixtures are frequently used to shorten set time and/or to allow thicker layers to be built up in a single pass.
Wet-Mix Applications: Pre-batched and thoroughly mixed repair material is placed into a concrete pump and transported via pump line to an exit nozzle where compressed air and admixtures, if any, are introduced. The repair material is propelled onto the prepared surface and consolidated by the force of the compressed air.
Material Requirements: pumpable, low-clump mixture which does not sag upon impact on the prepared substrate.
Next, let’s look at the steps in a shotcrete repair…
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
Which shotcrete method is more ideal for shallow applications?
Dry-mix shotcrete
Wet-mix shotcrete

## Slide 127: Shotcrete Application
Remove unsound concrete and prepare using the method covered earlier. Ensure that surface is SSD (saturate-surface dry). Do not use bonding agents in shotcrete applications.
1
Steps in process:
Bulletin
RAP-12
Notes: Whether you are using dry- or wet-process shotcrete, many of the steps in the application and the benefits are the same.
This technique is typically used on vertical surfaces such as columns (as seen here), wall, beams, pier caps or overhead horizontal surfaces such as ceilings, beam bottoms, slab soffits, and deck overhangs.
A huge advantage of this method is that the repair material is consolidated as it is applied. It’s typically used when forming requirements are difficult or prohibitively expensive from executing.
Proprietary products are available specifically for shotcrete applications.
In shotcrete applications, bonding agents are not advised. Bonding agents interfere with the shotcrete’s natural bonding mechanism and often create an unreliable and unpredictable bond or even a bond breaker.

## Slide 128: Shotcrete Application
Begin by spaying the corners with the repair material and continuously moving the nozzle to encapsulate around reinforcing steel and avoid build up of material in one spot.
2
Steps in process:
Additional layers of shotcrete can be placed in order to create desired thickness.
Bulletin
RAP-12
Notes: Begin by spaying the corners with the repair material and continuously moving the nozzle to encapsulate around reinforcing steel and avoid build up of material in one spot.
Additional layers of shotcrete can be placed in order to create desired thickness.

## Slide 129: Shotcrete Application
Excessive finishing is discouraged in these applications although rodding into straight lines is not a problem. Proper curing with curing compounds or moist curing will ensure a successful repair.
3
Steps in process:
Bulletin
RAP-12
Curing methods are outlined in ACI 3048R Guide to Curing Concrete.
Notes: Again, for more information on curing methods, refer to, ACI 3048R Guide to Curing Concrete.

## Slide 130: Shotcrete Application
Advantages:
Ideal for hard-to-reach locations
Ideal for covering large areas
Fast erection
Consolidates as it is applied without formwork.
Disadvantages:
Can be messy to clean up
Skilled, certified installer necessary
Often used when forming requirements are difficult or too expensive
Bulletin
RAP-12
Shotcrete Application: Things to Consider
Notes: This technique is typically used on vertical surfaces such as columns, walls, beams, pier caps, or overhead horizontal surfaces such as ceilings, beam bottoms, slab soffits, and deck overhangs.
A huge advantage of this method is that the repair material is consolidated as it is applied and does not require formwork for a self-consolidating placement. It’s typically used when forming requirements are difficult or prohibitively expensive from executing.
Proprietary products are available specifically for shotcrete applications.

## Slide 131: Crack Repair
As we covered before, some repairs do not require removal of concrete.
If no delamination is found, the repair methods differ.
Next, we will look at crack repair applications and the materials used to fix them.

## Slide 132: Materials for Crack Repairs
Viscosity refers to the thickness of a material and is measured in cps.
Peanut butter = 250 cps
Milk = 3 cps
Different materials are used for crack repairs.
Crack repair materials tend to have a lower viscosity in order to fully penetrate the depth of the repair.
Their low viscosity makes it easier for them to penetrate and fill cracks.
Notes: As covered earlier, crack repairs that are not caused by corrosion of the metal rebar and do not require the removal of concrete can use different repair materials. Often, repair materials for cracks typically have a lower viscosity in order to fully penetrate the full depth of the crack. For structural cracks, an injection method may be necessary.
It’s important to note that some of crack repair materials should only be used in non-moving cracks, or cracks that will not be subjected to moving forces.

## Slide 133: Types of Cracks
Is the crack moving or non-moving?
Structural
The crack compromises integrity of the structure
Non-Structural
The crack does not compromise the integrity of the structure
Non-moving
Crack will not move
Moving
Repair material allows for some movement of the cracks.
Should be fixed with a flexible material such as a sealant.
Non-moving cracks should be filled with an inflexible material such as an epoxy resin.
Some non-moving cracks can be non-structural
Notes: Whether or not the crack is moving or non-moving will dictate the type of repair material to use.
A non-moving crack, as it’s name suggests will not move. These cracks are typically structural and need to be filled because they compromise the integrity of the structure. Structural, non-moving cracks should be filled with a rigid material under pressure injection to ensure that all voids are completely filled. We will cover this pressure-injection application method later in the course.
Moving cracks, on the other hand, tend to be non-structural, meaning that they do not compromise the integrity of the structure. These cracks still need to be filled, however, as they provide a pathway for deteriorating agents. Moving cracks will constrict and expand for various reasons and should be fixed with a flexible material that will accommodate for some movement. If a moving crack is sealed with an inflexible material, they will possibly crack again adjacent to the repaired crack.

## Slide 134: Materials for Crack Repairs
Structural, non-moving cracks that are not associated with delaminated concrete, should be filled with a rigid material.
Examples:
  Epoxy Resins
  Polymer Mortars
  Polymer-Cement Mortars
  Cement Grouts
Notes: Epoxy resins are ideal for nonmoving cracks and can be applied by gravity feed or pressure injection.
Polymer mortars are ideal for non-moving cracks of 0.25” or greater in width and should be hand-applied and packed.
Polymer-cement mortars consist of fine aggregate, water, and polymer.
Cement grouts are a mixture of cement and water with or without admixtures. This material should be packed into the crack and finished flush with concrete.
___________
Quiz Note
This slide features information that will be found on the post-course knowledge assessment.
Which of the following crack repair materials would be suitable for a non-moving, structural crack?
Epoxy resins
Silicone sealants
Methyl-methacrylates
Polyurethane chemical grouts

## Slide 135: Materials for Crack Repairs
Non-structural, moving cracks should be able to accommodate for some movement.
Examples:
  Polyurethane Chemical Grouts
  Silicone Sealants
  Polysulfide Sealants
  Polyurethane (Urethane) Sealants
  Methacrylates
Notes: Polyurethane chemical grouts can be injected in vertical, overhead and horizontal cracks that are active or leaking.
Silicone sealants can be used in vertical, horizontal, or overhead applications.
Polysulfide sealants are used to treat moving and non-moving cracks in vertical or horizontal elements that are submerged and have excellent chemical resistence.
Polyurethane sealants treat moving and non-moving cracks in horizontal or vertical elements. A two-to-one joint width to depth ratio should be maintained during installation.
Methacrylates are typically flood coated and good for filling a large number of cracks in horizontal concrete slabs that have no indication of concrete delamination causef from rebar corrosion of an alkali-aggregate reaction.

## Slide 136: Crack Repair by Gravity Feed Resin
General Description: After crack is properly cleaned with compressed air to remove debris, dispense the epoxy until the void is completely filled.
Material Requirements: a non-moving structural material that is highly flowable.
Best Applications: horizontal, structural applications.
Crack Repair by Gravity Feed with Epoxy Resin
For more information, refer to:
ACI 546.3R-14 Guide to Materials Selection for Concrete Repair
ACI 224.1R Causes, Evaluation, and Repair of Cracks in Concrete Structures
ASTM C881 Standard Specification for Epoxy-Resin-Base Bonding systems for Concrete
For non-moving cracks
Bulletin
RAP-2
Notes: Play video.
All cracks must be prepared by cleaning the crack with compressed air to remove debris.
Dispense the epoxy resin into the repair material until it is level with the substrate. Although this is ideal for non-moving cracks, it may not always be suitable for all types of structural cracks. In general, it is best to place materials that seek to fix structural non-moving cracks with pressure injection that uses positive displacement (as we will look at in the next slide). Pressure injection ensures that there are no air pockets in the crack and that the crack is therefore completely sealed from moisture and other disintegrating agents.

## Slide 137: Crack Repair by Epoxy Pressure Injection
For more information, refer to:
ACI 546.3R-14 Guide to Materials Selection for Concrete Repair
ACI 224.1R Causes, Evaluation, and Repair of Cracks in Concrete Structures
ASTM C881 Standard Specification for Epoxy-Resin-Base Bonding Systems for Concrete
Crack Repair by Epoxy Pressure Injection
General Description: Crack is filled under pressure through ports.
Material Requirements: flowable, pumpable, non-moving material.
Best Applications: vertical/overhead structural cracks.
For non-moving cracks
Bulletin
RAP-1
Notes: Play video.
After applying ports along the crack, inject the epoxy from the lowest port until that port is filled. Move to next port, and continue until entire crack is filled. Break off ports and finish repair.
As a rule of thumb, injection ports should be placed eight inches apart along the length of the crack.
When applying puddy along the length of the crack, take care to mound the epoxy around the base of the port to approximately ¼ of an inch thick, extending 1 inch out from the base of the port to work out any hole I the material. It is recommended that the paste-over should be a minimum of 3/16 of an inch thick and 1 inch wide along the crack. Insufficient past-over will result in leaks under the pressure of injection. If the crack passes completely through the concrete element, seal the back of the concrete is possible. If you do not do this, the epoxy may be run out the backside of the crack resulting in an ineffective repair.
Inject epoxy into the first port until it will no longer fill into the crack. If epoxy shows at the next port and the first port still accepts the material, close the second port and continue to inject into the first port until to accepts no more epoxy.
Continue closing ports where epoxy appears until the first port refuses epoxy.

## Slide 138: Crack Repair Rout and Seal
Rout-and-Seal Applications
General Description: Sometimes known as “crack chasing,” this method uses a saw or router to create a recess over an existing crack. It is then filled with cementitious material or epoxy paste.
Material Requirements: cementitious material or epoxy paste.
Best Applications: non-moving, horizontal crack.
For more information, refer to:
ACI 224.1R Causes, Evaluation, and Repair of Cracks in Concrete Structures
For non-moving cracks
Notes: Rout and seal application are used for non-moving cracks. This application uses a saw or router to create a recess over an existing crack. Since these are non-moving cracks, they can be filled with a cementitious material or epoxy paste.
It is essential to seal these cracks to prevent the intrusion of moisture and chlorides. Sealing these cracks can slow deterioration of the structure and protect the rebar from corrosive agents.

## Slide 139: Crack Repair: Flood Coating
Methyl-Methacrylate Flood Coating
General Description: Hairline cracks that are not associated with delamination can be filled by pouring a low-viscosity, methyl-methacrylate material over the properly prepared area.
Material Requirements: extremely low-viscosity repair material. Sand is sometimes broadcast over the area after material is poured to decrease slipping potential.
Best Applications: horizontal surfaces with shallow, hairline cracks that show no evidence of steel rebar corrosion. Be sure to not use in sloped areas where material could pool.
For more information, refer to:
ACI 224.1R Causes, Evaluation, and Repair of Cracks in Concrete Structures
For non-moving cracks
Bulletin
RAP-13
Notes: Hairline cracks in concrete can occur from a variety of causes. Typically on roads such as this, they can be caused from abrasion (thousands of cars driving over this surface every day), freeze-thaw cycles, or deicing salts. When there are thin cracks, its not always feasible to fill these cracks individually. Therefore, a flood coating it sometimes used. Flood-coating applications pour a very thin repair material (think thin glue) over the surface. The low-viscosity material will then penetrate many hairline cracks at once and seal them from further deteriorating agents.
Methyl-methacrylates are particularly ideal for this type of application.
Take care not to use this method in sloped areas where the repair material will not be evenly distributed.
First the surface is shot- or sand-blasted and debris is removed from the surface using compressed air. Then the thin, low-viscosity repair material is poured over the surface. The resin should be allowed to pond over the cracks until they are completely filled. Excess resin should be removed before it has gelled.
Often sand is broadcast over the surface to make the area slip resistance and give it a rough finish.

## Slide 140: Moving Cracks
Now we’ll take a look at how to repair moving cracks…
Remember, generally moving cracks are non-structural and need to be filled with a flexible, rubbery material that can accommodate for movement.
Possible repair materials for moving cracks include:
Polyurethane grouts or sealants
Polysulfide sealants
Silicone sealants

## Slide 141: Moving Cracks
When applying repair material to moving cracks there should be no “three-sided adhesion.”
This is done so that the material can expand and contract horizontally without putting pressure on the bottom of the crack.
Here the repair material is only attached to two sides of the cracked substrate.
Repair material can be applied using a backer rod or bond breaker tape to prevent the repair material from adhering to the bottom of the crack.

## Slide 142: Checkpoint Questions
Which of the following repair placement methods would require additional consolidation with a vibrator?
Form and pour
Form and pump
Shotcrete
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 143: Checkpoint Questions
Which of the following repair placement methods would require additional consolidation with a vibrator?
Form and pour
Form and pump
Shotcrete
Shotcrete and form-and-pump applications apply the repair material under pressure and are both self-consolidating.
Form-and-pour applications, however, would require consolidation after the repair material is placed to ensure that there are no air pockets in the placed material.
Notes: Time provided, ask these Check Your Knowledge Questions. You can hide questions that you do not want to ask prior to the presentation.

## Slide 144: Section Review
The application method should be selected based on the repair’s accessibility, constructability, and material, owner, and service requirements.
Properly preparing and executing the repair will increase the likelihood of a lasting solution.
To review:

## Slide 145: In Closing

## Slide 146
Assess
1
Plan
2
Prepare
3
Execute
4
There are many variables to take into consideration at each step along the way.
Remember to follow the four-step process introduced at the beginning of the course.
Notes: Assessing the damaged concrete, selecting the materials and methods, and planning the repair… none of these are easy!
There are many variables to take into consideration at each step along the way.
Remember to follow the four step process introduced at the beginning of the course, assess, plan, prepare, and execute.

## Slide 147: References
Technical Guidelines and Reference From:
American Concrete Institute (ACI)
International Concrete Repair Institute (ICRI)
American Society for Testing and Materials (ASTM)
American Association of State Highways and Transportation Officials (AASHTO)
Portland Cement Association (PCA)
IHS Standards Store
Other Resources:
Emmons, Peter H. Concrete Repair and Maintenance Illustrated: Problem Analysis, Repair Strategy, Techniques. Kingston, MA: R.S. Means, 1993. Print.
Notes: Direct participants to these industry standard websites as great resources when designing, planning, and executing a repair.

## Slide 148: Course Completion
Simpson Strong-Tie
This concludes the continuing education course.
For a library of Simpson Strong-Tie courses,
visit strongtie.com/workshops
Notes: Do
Draw the meeting to a close. Hand out literature and business cards.
Say
If you have ongoing projects that you would be interested in reviewing together, please let me know.

## Slide 149: Next Steps!
AIA: For those seeking AIA LU/HSW: You will receive an email with a link allowing access to print your Certificate. Congratulations, you will have earned 2 LU/HSW credits. If your AIA member number has been inserted into your profile, Simpson Strong-Tie will report your credits on your behalf to the AIA. No test is required in order to receive HSW credits.
IACET: For those seeking IACET CEUs: You will receive an email with a link allowing access to print your Certificate of Attendance and instructions directing you to the Simpson Student Center to take the exam before credits can be awarded. Once the exam is taken and passed, you will have earned 0.2 CEUs (2 hours of credit). You can then access your Certificate of Completion from the Course Content tab. You must self-report your credits to your certifying organization or agency.
If you have questions or need assistance, please contact training@strongtie.com.
Notes: Presenter Notes:
Review the email and notification process as outlined in this slide.
AIA LUs:
For those that want AIA HSW credit, be sure to provide your AIA number on the sign-in sheet and Simpson will report your credits to the AIA on your behalf.
No test is required for AIA credit.
CEUs:
For those seeking CEUs, watch for an email with instructions to access the online test. After you have passed the test, you may access your Certification of Completion from the course content tab.
You must self-report your credits to your certifying organization or agency.

## Slide 150: Next Steps!
ICC: For those seeking ICC CEUs: You will receive an email with a link allowing access to print your Certificate. Congratulations, you will have earned 0.2 ICC CEU (2 hours of credit). Please make sure your ICC member number has been inserted into your profile. It is your responsibility to self-report your credits to the ICC. Please retain your Completion Certificate for your records.
IACET: For those seeking IACET CEUs: You will receive an email with a link allowing access to print your Certificate of Attendance and instructions directing you to the Simpson Student Center to take the exam before credits can be awarded. Once the exam is taken and passed, you will have earned 0.2 CEUs (2 hours of credit). You can then access your Certificate of Completion from the Course Content tab. You must self-report your credits to your certifying organization or agency.
If you have questions or need assistance, please contact training@strongtie.com.
Notes: Presenter Notes:
Review the email and notification process as outlined in this slide.
Watch for an email directing you to the Student Center to print your certificate.
No test is required for ICC credit. You must self-report your credits to ICC.
For those seeking general IACET CEUs after you have passed the online test, you may access your Certification of Completion from the course content tab. You must self-report your credits to your certifying organization or agency.